## Introduction
NECB 2011 Part 5 and Part 6 - HVAC Trade-Off Path and DHW Trade-Off Path Compliance Calculation Tool
This tool allows the demonstration of compliance with NECB 2011 when using the Part 5 and/or Part 6 Trade-off path. Users must define all of the systems in the building along with their component characteristics for the output to be valid. The HVAC and SWH indices indicate whether a system passes or fails. Only cells highlighted in BLUE need to be filled. This tool does not calculate the actual energy use index of a system but only its compliance to the NECB 2011 trade-off path.
Building Data
Building Name
| Climate Zone | Zone 7B
Address
Building Conditioned Area - m2
Applicant Name
Applicant Address
Applicant Phone #
| Language | English
| Units | SI
This tool is the property of Natural Resources Canada.All rights reserved. No part of this Tool may be reproduced, modified, distributed, published, sold, licensed, broadcasted, retransmitted, circulated in any form or used this tool in any way other than for compliance to the 2011 NECB.

## HVAC-CVCA
Compliance of the heating, ventilating and air-conditioning systems (HVAC)
Building Compliance: | HVAC system deemed to comply with Section 5.3
HVACTOI |  | 0.03518
Compliance: |  | System is NECB Compliant
HVAC Type ID - #1
System Type: |  | Built-up variable-volume
Cooling System Type: |  | Room Air Conditioners and Room Air Conditioner Heat Pumps
Cooling Sub-System Type: |  | Room air conditioners with reserve cycle with louvered sides < 10.55 (36000)
Cooling capacity: | W | 3515.9684
Heating System Type: |  | Electric boilers
Component | Units | Components Efficiencies
Supply fan mechanical efficiency | % | 60%
Supply motor efficiency | % | 91.67%
Return fan mechanical efficiency | % | 38%
Return fan motor efficiency | % | 80%
Supply temperature control | Selection | Supply OA Reset
Airflow control efficiency | Selection | Forward curve with vanes
Supply fan total static pressure | Pa | 996.36
Supply duct insulation | RSI Value | 0.58
Return fan total static pressure | Pa | 249.09
Heating coil design temperature drop | °C | 11.1111
Baseboard heater design temperature drop | °C | 11.1111
Boiler/furnace/heat pump heating efficiency | Fraction | 1
Chillers/direct expansion system/heat pump cooling efficiency | COP | 2.4905
Rejection fan input power ratio | W/W | 0.051195
Cooling by direct use of outdoor air (air economizer) | Selection | Dual DBT
Outdoor airflow control | Selection | Fixed
Exhaust air heat-recovery efficiency | % | 0%
Cooling by indirect use of outdoor air (water economizer) | % | 0%
Piping insulation - hot water | RSI Value | 0.88059
Piping insulation - chilled water | RSI Value | 0.88059
Piping pressure losses - hot water | kPa | 179.34
Piping pressure losses - chilled water | kPa | 119.56
Pump mechanical efficiency - hot water | % | 60%
Pump mechanical efficiency - chilled water | % | 60%
Pump motor efficiency - hot water | % | 90%
Pump motor efficiency - chilled water | % | 90%
Hot water pump control | Selection | Snap outdoor
Chilled water pump control | Selection | Snap outdoor
Hot water loop temperature control | Selection | OA Reset, min >140 °F
Chilled water loop temperature control | Selection | OA Reset, min <54 °F
Hot water flow control | Selection | Constant
Chilled water flow control | Selection | Two speed, .5, fixed
8
Net impact
3.519%
Selected HVAC
1
Reference Efficiencies
0.6
0.91667
0.38
0.8
0.5
0.55698
4
3.2932
1
20
20
1
2.4905
0.015
0.8
0
0
0
5
5
60
40
0.6
0.6
0.9
0.9
0.8
0.8
0.8
0.8
0.8
0.8
Component
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
HDD/CDD/TDD for a's
HDD
HDD
HDD
HDD
HDD
TDD
HDD
HDD
HDD
HDD
HDD
HDD
HDD
TDD
CDD
TDD
TDD
CDD
TDD
CDD
HDD
CDD
TDD
CDD
HDD
CDD
HDD
CDD
HDD
CDD
TDD
CDD
Applicability to system
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
1
b0
0.99011
0.69938
0.60873
0.2916
-0.21746
0.10343
-0.064035
0.0163
-0.077256
0
0
0.77478
0.074364
0.11209
99.5152
-1.162
0.026827
-0.011932
0.088391
2.7067e-05
-0.0001786
4.4626e-05
0.04106
-0.01101
0.027826
-0.0037224
-131.4748
-0.21746
40.9117
-5.6007
-133.6625
-2.4991
b1
-0.00014178
-0.00010125
-5.5134e-05
-2.7124e-05
0.00016105
3.422e-05
1.1795e-05
-3.7735e-06
9.584e-06
0
0
2.1285e-06
3.2082e-06
-0.00016605
-0.46855
2.1738e-05
-2.5286e-05
8.378e-05
-2.0985e-05
5.5148e-06
-1.7419e-08
-1.3555e-06
9.9307e-06
0.00030371
7.041e-06
0.00015204
0.048216
0.00016105
-0.01309
0.013251
0.05146
0.032644
b2
5.7105e-09
4.0546e-09
7.3517e-10
3.9718e-10
-1.9762e-08
-3.997e-09
-6.0965e-10
2.4165e-10
-3.2999e-10
0
0
3.7633e-09
-1.108e-09
1.652e-08
0.00046015
6.8452e-09
5.1761e-09
-1.1966e-07
1.3451e-09
-7.0919e-09
1.2819e-12
1.6429e-09
-8.2825e-10
-3.6644e-07
-5.3517e-10
-1.593e-07
-3.9042e-06
-1.9762e-08
9.2719e-07
1.2808e-05
-4.3932e-06
-5.4833e-05
c0
-0.51911
-0.26704
-0.52436
-0.12641
1.0814
0.81096
0.0019764
-0.0016946
0.0048486
0
0
0
-0.0044639
-0.43222
-63.6506
1.2986
-0.028839
0.016237
-0.0060714
7.6532e-06
1.9485e-07
-1.6991e-08
-0.021567
0.0068313
-0.010491
0.0012069
79.7918
1.0814
-23.1669
3.552
83.2734
1.4812
c1
7.0367e-05
3.687e-05
4.3243e-05
1.0953e-05
-0.00034476
-0.00020762
-4.9231e-07
3.8904e-07
-1.1263e-06
0
0
0
-2.3342e-07
0.00018843
0.30513
-1.2103e-06
2.113e-05
-2.1651e-05
1.4518e-06
-2.8917e-07
-4.4861e-11
-7.2959e-10
-6.0291e-06
-0.0001741
-2.6714e-06
-5.5162e-05
-0.028984
-0.00034476
0.0076326
-0.004414
-0.031825
-0.016384
c2
-2.626e-09
-1.362e-09
-2.1529e-10
-8.6199e-11
2.8874e-08
1.3528e-08
3.0465e-11
-2.4707e-11
6.5972e-11
0
0
0
7.0258e-11
-1.5814e-08
-0.00030307
-7.954e-09
-3.5018e-09
2.748e-08
-9.1345e-11
3.2009e-10
4.2018e-15
1.2425e-12
5.1058e-10
2.0938e-07
1.989e-10
5.2642e-08
2.3417e-06
2.8874e-08
-5.4418e-07
-1.3427e-05
2.7173e-06
2.9382e-05
HDD/CDD/TDD for a's
6500
6500
6500
6500
6500
6900
6500
6500
6500
6500
6500
6500
6500
6900
400
6900
6900
400
6900
400
6500
400
6900
400
6500
400
6500
400
6500
400
6900
400
b
0.30978
0.21253
0.28143
0.13207
-0.0056288
0.14925
-0.013123
0.0019817
-0.028901
0
0
0.94761
0.048405
-0.24716
-14.282
-0.68611
0.098786
0.0024351
0.0076292
0.0010983
-0.00023766
-0.00023471
0.070149
0.051844
0.050982
0.031605
16.9728
-0.1562
-4.9986
1.7491
12.2507
1.7852
c
-0.17267
-0.084924
-0.25238
-0.05886
0.060403
0.022474
6.3511e-05
-0.00020968
0.000315
0
0
0
-0.0030128
0.11504
9.9101
0.91151
-0.04976
0.011973
-0.00040307
-5.68e-05
8.0771e-08
-1.1002e-07
-0.038859
-0.029307
-0.019452
-0.012435
-9.6677
0.94815
3.4534
-0.36193
-6.953
-0.37127
Corrected Component Efficiency
12.37%
12.35%
7.05%
6.799%
4.748%
9.01%
-5.148%
0.4252%
-2.859%
0%
0%
94.76%
10.19%
-0.3682%
-508.3%
0%
0%
0%
2.807%
0.4071%
-1.397%
-0.9564%
2.81%
2.056%
3.013%
1.837%
739.1%
48.19%
-178.9%
116.8%
535.1%
119.1%
0.93437
0.55698
0.8
0
0.8
0.8
0.8
0.8
0.8
0.8
Base efficiency
0.1237
0.12346
0.070499
0.067987
0.012286
0.090103
-0.051476
0.0042521
-0.028586
0
0
0.94761
0.10187
-0.0036815
-5.0832
0
0
0
0.028069
0.0040714
-0.013969
-0.0095645
0.0281
0.020556
0.030128
0.018372
7.3909
0.48185
-1.7887
1.1676
5.3507
1.1906
Net
0%
0%
0%
0%
3.519%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
0%
Cooling Equip Eff
2.9111
2.8511
3.1086
2.4905
Ranges - Min
Supply fan mechanical efficiency |  | 0.3
Supply motor efficiency |  | 0.3
Return fan mechanical efficiency |  | 0.2
Return fan motor efficiency |  | 0.3
Supply temperature control |  | 0.5
Airflow control efficiency |  | 0.21
Supply fan total static pressure |  | 0
Supply duct insulation |  | 0
Return fan total static pressure |  | 75
Heating coil design temperature drop |  | 0.06
Baseboard heater design temperature drop |  | 0.06
Boiler/furnace/heat pump heating efficiency |  | 0.3
Chillers/direct expansion system/heat pump cooling efficiency |  | 0.5
Rejection fan input power ratio |  | 0
Cooling by direct use of outdoor air (air economizer) |  | 0.76
Outdoor airflow control |  | 0
Exhaust air heat-recovery efficiency |  | 0
Cooling by indirect use of outdoor air (water economizer) |  | 0
Piping insulation - hot water |  | 0
Piping insulation - chilled water |  | 0
Piping pressure losses - hot water |  | 0.3
Piping pressure losses - chilled water |  | 0.3
Pump mechanical efficiency - hot water |  | 0.4
Pump mechanical efficiency - chilled water |  | 0.4
Pump motor efficiency - hot water |  | 0.3
Pump motor efficiency - chilled water |  | 0.3
Hot water pump control |  | 0.8
Chilled water pump control |  | 0.79
Hot water loop temperature control |  | 0.79
Chilled water loop temperature control |  | 0.78
Hot water flow control |  | 0.8
Chilled water flow control |  | 0.8
Ranges - Max
Supply fan mechanical efficiency |  | 0.9
Supply motor efficiency |  | 0.99
Return fan mechanical efficiency |  | 0.6
Return fan motor efficiency |  | 0.99
Supply temperature control |  | 1
Airflow control efficiency |  | 0.6
Supply fan total static pressure |  | 2241.81
Supply duct insulation |  | 1.06
Return fan total static pressure |  | 1245.45
Heating coil design temperature drop |  | 27.78
Baseboard heater design temperature drop |  | 27.78
Boiler/furnace/heat pump heating efficiency |  | 3
Chillers/direct expansion system/heat pump cooling efficiency |  | 8
Rejection fan input power ratio |  | 3.41
Cooling by direct use of outdoor air (air economizer) |  | 0.8
Outdoor airflow control |  | 0.93
Exhaust air heat-recovery efficiency |  | 0.9
Cooling by indirect use of outdoor air (water economizer) |  | 0.99
Piping insulation - hot water |  | 1.59
Piping insulation - chilled water |  | 1.59
Piping pressure losses - hot water |  | 448.35
Piping pressure losses - chilled water |  | 448.35
Pump mechanical efficiency - hot water |  | 0.7
Pump mechanical efficiency - chilled water |  | 0.7
Pump motor efficiency - hot water |  | 0.99
Pump motor efficiency - chilled water |  | 0.99
Hot water pump control |  | 0.86
Chilled water pump control |  | 0.81
Hot water loop temperature control |  | 0.87
Chilled water loop temperature control |  | 0.83
Hot water flow control |  | 0.81
Chilled water flow control |  | 0.81

## SWH-CES
Compliance of the service water heating (SWH) systems
Building Compliance: | The SWH system is deemed to comply with Section 6.3
0
0 |  | The sum of the faucet flow ratio and the shower flow ratio must not exceed 100%.
SWHTOI |  | 0
Compliance: |  | System is NECB Compliant
SWH Type ID - #1
System Type: |  | Tank
Equipment Type: |  | Electric
Tank Volume: | L | 60
Component | Units | Component Efficiency
Service water heating equipment efficiency | % | 98%
Tank insulation value | RSI Value | 2.1839
Piping insulation value | RSI Value | 0.67735
Pump motor efficiency | % | 80%
Pump efficiency | % | 60%
Heat recovery ratio | W/W | 0
Average flow of all faucets | L/min | 8.327
Average flow of all showers | L/min | 9.4625
Average flow of other uses | L/min | 7.6
Faucet flow ratio | % | 50%
Shower flow ratio | % | 50%
| Selected | 0
| SWH-1 | 0
| SWH-2 | 0
| SWH-3 | 0
| Anorm | 11.4525
| Dnorm | 0.81413
| PDR | 1
| Ref | 98%
| Gas-fired < 22 kW | 0.64
| Gas-fired 22 - 117 kW | 0.64
| Oil-fired, instantaneous, ≤ 61.5 kW | 0.476
| Ref Tank+Instantaneous | 0.98
| Ref Boiler | #N/A
| Sys Type | 1
Reference values
| Tank volume | 60
| Service water heating equipment efficiency | 0.98
| Tank insulation value | 2.1839
| Piping insulation value | 0.67735
| Pump motor efficiency | 0.8
| Pump efficiency | 0.6
| Heat recovery ratio | 0
| Average flow of all faucets | 8.327
| Average flow of all showers | 9.4625
| Average flow of other uses | 7.6
| Faucet flow ratio | 50%
| Shower flow ratio | 50%
Data Ranges Min
| Service water heating equipment efficiency | 0.2
| Tank insulation value | 0.02
| Piping insulation value | 0.02
| Pump motor efficiency | 0.1
| Pump efficiency | 0.1
| Heat recovery ratio | 0
| Average flow of all faucets | 0.006309
| Average flow of all showers | 0.006309
| Average flow of other uses | 0
| Faucet flow ratio | 0
| Shower flow ratio | 0
Data Ranges Max
| Service water heating equipment efficiency | 10
| Tank insulation value | 7.04
| Piping insulation value | 7.04
| Pump motor efficiency | 0.99
| Pump efficiency | 0.7
| Heat recovery ratio | 1
| Average flow of all faucets | 15.14
| Average flow of all showers | 10
| Average flow of other uses | 378.5
| Faucet flow ratio | 1
| Shower flow ratio | 1

## Tables (hidden)
# of Systems | 1 | Call for HVAC-CVCA Sheet Worksheet_Change Function from sheet not from macro | TRUE | # SWH | 1 | Call for SWH-CES Sheet Worksheet_Change Function from sheet not from macro | TRUE
Current Language (1: English, 0: French) | 1 | Current units (1: SI, 0 : IP) | 1 | [96 empty] | Table 5.3.2.8 | [58 empty] | Climate Zones
| Table 5.3.1.1: Types of HVAC Systems |  |  | Table 5.3.2.2 | [28 empty] | Table 5.3.2.3 |  | Table 5.3.2.4 | [27 empty] | Table 5.2.12.1 - Heating |  |  |  | Table 5.2.12.1 - Cooling |  |  | Table 5.3.2.7 | [32 empty] | Parameter | [15 empty] | Menu |  | Pass_Fail |  | Choice |  | DHW Eff Table |  |  | SHW ToV |  | DHW Sys Type |  |  |  | General | Intro |  |  | HVAC Help Table |  | Pass_Fail |  | Units Label | Conversion (IP value * factor = SI) | Titre |  |  | SWH Help Table |  | Titres |  |  |  | Reports |  | Reports |  | Reports |  | City / Location | Province/Territory | Zone
| Built-up variable-volume | 1 |  |  | System | [27 empty] | Supply fan mechanical efficiency |  |  | System | [26 empty] | Electric boilers | 100% |  |  | Air Cooled Unitary Central Air-Conditioners and Heat Pumps - Electrically Operated |  |  |  |  | System | [27 empty] | System | ToV | Index | α1 | α2 | α3 | β1 | β2 | β3 |  | Location | HDD | CDD | TDD | Location Data |  | Units Label | Conversion (IP value * factor = SI) |  | System Type: |  | HVAC system deemed to comply with Section 5.3 |  | Yes |  | Electric | 0.98 |  | Service water heating equipment efficiency |  | Tank |  | (m2): |  | Français | This tool allows the demonstration of compliance with NECB 2011 when using the Part 5 and/or Part 6 Trade-off path. Users must define all of the systems in the building along with their component characteristics for the output to be valid. The HVAC and SWH indices indicate whether a system passes or fails. Only cells highlighted in BLUE need to be filled. This tool does not calculate the actual energy use index of a system but only its compliance to the NECB 2011 trade-off path. |  |  | Enter the supply fan design mechanical efficiency. |  | The SWH system is deemed to comply with Section 6.3 |  | % | 1 | System Type: |  |  | Select the system type that most closely matches the one being evaluated. |  | Compliance of the service water heating (SWH) systems |  | Compliance of the heating, ventilating and air-conditioning systems (HVAC) |  | Statement of Compliance – National Energy Code of Canada for Buildings 2011 Summary Compliance Report to NECB Part 5 - HVAC |  | Statement of Compliance – National Energy Code of Canada for Buildings 2011 Summary Compliance Report to NECB Part 6 - SWH |  | System |  | Vancouver | Br. Columbia | 4 |  | This tool is the property of Natural Resources Canada.All rights reserved. No part of this Tool may be reproduced, modified, distributed, published, sold, licensed, broadcasted, retransmitted, circulated in any form or used this tool in any way other than for compliance to the 2011 NECB.
| Constant-volume reheat | 2 |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 |  | Supply motor efficiency |  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | Gas-fired boilers, < 88 kW | 85% | AFUE |  | Single-Package Vertical Air Conditioners (SPVAC) and Heat Pumps (SPVHP) |  |  | ToV | Parameter | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 |  | 1 | 1 | 1 | 0.99011 | -0.00014178 | 5.7105e-09 | -0.51911 | 7.0367e-05 | -2.626e-09 | HDD | Zone 4 | 2900 | 250 | 3150 | Location | Zone 7B | % | 1 |  | Cooling System Type: |  | HVAC system does not comply with Section 5.3 |  | No |  | Heat pump water heaters | 2.1 |  | Tank insulation value |  | Tankless (instantaneous) |  |  |  | English |  |  |  | Enter the supply fan motor design efficiency. |  | The SHW system does not comply with Section 6.3 |  | RSI Value | 0.17612 | Equipment Type: |  |  | Select the type of equipment used in producing the service hot water. | [5 empty] | Project Name: |  | Project Name: |  |  |  | Abbotsford | Br. Columbia | 5
| Packaged single duct - single zone | 3 |  | ToV1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 |  | Return fan mechanical efficiency |  | BaV1 | 60% | 60% | 44% | 54.55% | 60% | 49.09% | 60% | 49.09% | 60% | 60% | 49.09% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 65% | 65% | 65% | 43.64% | 60% | 65% | 54.55% | 54.55% | 60% | Gas-fired boilers, >= 88 kW and < 733 kW | 83% | Et |  | Evaporatively Cooled and Water Evaporatively Cooled Unitary Air Conditioners and Heat Pumps - Electically Operated |  |  | 5 | Supply OA Reset | 0.93437 | 0.349 | 0.91805 | 0.91805 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93437 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 |  | 1 | 2 | 2 | 0.69938 | -0.00010125 | 4.0546e-09 | -0.26704 | 3.687e-05 | -1.362e-09 | HDD | Zone 5 | 3500 | 550 | 4050 | HDD | 6500 | % | 1 |  | Cooling Sub-System Type: |  | Incomplete data entry |  |  |  | Gas-fired < 22 kW | -1 |  | Piping insulation value |  | Space-heating boiler |  |  |  |  | French | English |  | Enter the return fan design mechanical efficiency. |  | Incomplete data entry |  | RSI Value | 0.17612 | Tank Volume: | 3.785 |  | Total volume of all storage tanks included in this system. Value must be equal or greater than 0. | [5 empty] | Project Address: |  | Project Address: |  |  |  | Tofino | Br. Columbia | 5
| Built-up single duct - single zone | 4 |  | ToV2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 |  | Return fan motor efficiency |  | BaV2 | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | 91.67% | Gas-fired boilers, >= 733 kW | 83.3% | Ec |  | Condensing Units |  |  | 5 | Warmest | 1 | 0.42528 | 0.73026 | 0.73026 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | 1 | 3 | 3 | 0.60873 | -5.5134e-05 | 7.3517e-10 | -0.52436 | 4.3243e-05 | -2.1529e-10 | HDD | Zone 6 | 4500 | 500 | 5000 | CDD | 400 | % | 1 |  | Cooling capacity: | [5 empty] | Gas-fired 22 - 117 kW | -2 |  | Pump motor efficiency |  |  |  | (m2) : | (m2): | SI | Cet outil permet de démontrer la conformité selon la méthode des solutions de remplacement pour la Partie 5 et la Partie 6 du CNÉB 2011. L’utilisateur doit définir tous les systèmes du bâtiment ainsi que les caractéristiques de toutes leurs composantes pour que le résultat soit valide. Les indices de solution de remplacement CVCA et SWH, indiquent si un système est conforme ou non-conforme au CNÉB. Seulement les cellules surlignées en BLEU doivent être remplies. L'outil ne sert pas à établir un indice de consommation réel d'un système mais uniquement à déterminer sa conformité au CNÉB 2011 selon la méthode des solutions de remplacement. | This tool allows the demonstration of compliance with NECB 2011 when using the Part 5 and/or Part 6 Trade-off path. Users must define all of the systems in the building along with their component characteristics for the output to be valid. The HVAC and SWH indices indicate whether a system passes or fails. Only cells highlighted in BLUE need to be filled. This tool does not calculate the actual energy use index of a system but only its compliance to the NECB 2011 trade-off path. |  | Enter the return fan motor design efficiency. |  |  |  | % | 1 |  |  |  | Enter the efficiency of the equipment used in producing the service hot water. For heat pumps, enter the COP in terms of %. For Efficiency Factors (EF), enter directly that value except for electric hot water tanks where an efficiency of 100% is to be used. If more than one equipment of the same type serves a system, enter the capacity-weighted average efficiency. Value must be greater than 0. | [5 empty] | Applicant Name: |  | Applicant Name: |  | Système | System | Penticton | Br. Columbia | 5
| Packaged variable-volume | 5 |  | ToV3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 |  | Supply temperature control |  | BaV3 | 38% | 37.5% | 31% | 31.25% | 37.5% | 25% | 37.5% | 25% | 30% | 37.5% | 25% | 37.5% | 37.5% | 37.5% | 37.5% | 37.5% | 37.5% | 37.5% | 37.5% | 37.5% | 37.5% | 31.25% | 37.5% | 37.5% | 31.25% | 31.25% | 37.5% | Oil-fired boilers, < 88 kW | 84.7% | AFUE |  | Water-Cooled Unitary Air Conditioners and Heat Pumps - Electrically Operated |  |  | 5 | Constant > 15°C | 0.86229 | 0.32275 | 0.91811 | 0.91811 | 0.86229 | 0.86229 | 0.86229 | 0.86229 | 0.86229 | 0.86229 | 0.86229 | 0.86229 | 0.86229 | 0.86229 | 0.86229 | 0.86229 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 | 0.86 |  | 1 | 4 | 4 | 0.2916 | -2.7124e-05 | 3.9718e-10 | -0.12641 | 1.0953e-05 | -8.6199e-11 | HDD | Zone 7A | 5500 | 450 | 5950 | TDD | 6900 | % | 1 |  | Heating System Type: | [5 empty] | Gas-fired > 117 kW | 0.77 |  | Pump efficiency | [5 empty] | IP |  |  |  | Choose from the drop down list the type of supply temperature control applicable to this HVAC system. |  |  |  | % | 1 |  |  |  | Define the tank's insulating value. For systems with multiple tanks, enter the surface-weighted average insulating value. Value must be between R 0.1 and 40 (RSI 0.5678-7.04). | [5 empty] | Applicant Address: |  | Applicant Address: |  |  |  | Penticton | Br. Columbia | 5 |  | Cet outil est la propriété de Ressources naturelles Canada. Tous droits réservés. Il est interdit de modifier, de distribuer, de publier, de vendre, de concéder par licence, de diffuser, de retransmettre, de mettre en circulation et d'utiliser cet outil sous quelque forme autres que celles prévues aux fins de vérification de conformité au CNÉB 2011. | This tool is the property of Natural Resources Canada.All rights reserved. No part of this Tool may be reproduced, modified, distributed, published, sold, licensed, broadcasted, retransmitted, circulated in any form or used this tool in any way other than for compliance to the 2011 NECB.
| Packaged constant-volume with reheat | 6 |  | ToV4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 |  | Airflow control efficiency |  | BaV4 | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | 80% | Oil-fired boilers, >= 88 kW and < 733 kW | 83.4% | Et |  | Direct-expansion ground-source heat pumps <= 21 (71700) |  |  | 5 | Constant <= 15°C | 0.5 | 0.2 | 0.94 | 0.94 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.94 | 0.5 | 0.5 | 0.94 | 0.94 | 0.5 |  | 1 | 5 | 5 | -0.21746 | 0.00016105 | -1.9762e-08 | 1.0814 | -0.00034476 | 2.8874e-08 | HDD | Zone 7B | 6500 | 400 | 6900 |  |  | Selection | 1 | [7 empty] | Oil-fired, instantaneous, <= 61.5 kW | -3 |  | Heat recovery ratio | [9 empty] | Choose from the drop down list the type of supply airflow control applicable to this HVAC system. |  |  |  | W/W | 1 |  |  |  | Define the average piping insulation value for this service water heating system. Value must be between R 0.1 and 40 (RSI 0.5678-7.04). | [5 empty] | Applicant Phone: |  | Applicant Phone: |  |  |  | Port Hardy | Br. Columbia | 5
| Built-up ceiling bypass VAV | 7 |  | ToV5 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 |  | Supply fan total static pressure |  | BaV5 | 0.5 | 0.2 | 0.943 | 0.943 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.943 | 0.5 | 0.5 | 0.943 | 0.943 | 0.5 | Oil-fired boilers, >= 733 kW | 85.8% | Ec |  | Packaged Terminal Air Conditioners (PTAC) and Heat Pumps (PTHP) |  |  | 6 | Forward curve with vanes | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 |  | 1 | 6 | 6 | 0.10343 | 3.422e-05 | -3.997e-09 | 0.81096 | -0.00020762 | 1.3528e-08 | TDD | Zone 8 | 8900 | 150 | 9050 |  |  | Selection | 1 | [7 empty] | Oil-fired, instantaneous, Vt < 37.8 L | 0.8 |  | Average flow of all faucets | [9 empty] | Enter the supply fan design total static pressure. It is important not to enter the external static pressure value, sometimes indicated on the equipment specifications. |  |  |  | L/min | 3.785 |  |  |  | Enter the efficiency of all pump motors used on this service water heating system. When multiple pumps are present, define the capacity-weighted average efficiency for all the pump motors. Value must be between 30% and 99%. | [5 empty] | General information |  | General information |  |  |  | Windsor | Ontario | 5
| Packaged ceiling bypass VAV | 8 |  | ToV6 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Supply duct insulation |  | BaV6 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | 0.55698 | Oil-fired boilers, residulal (No.5 or No.6 oil) and other, < 88 kW | 84.7% | AFUE |  | Room Air Conditioners and Room Air Conditioner Heat Pumps |  |  | 6 | VSD | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 |  | 1 | 7 | 7 | -0.064035 | 1.1795e-05 | -6.0965e-10 | 0.0019764 | -4.9231e-07 | 3.0465e-11 | HDD | [6 empty] | Pa | 249.09 | [7 empty] | Oil-fired, instantaneous, Vt >= 37.8 L | 0.77 |  | Average flow of all showers | [9 empty] | Enter the average insulation value for the supply ducts served by this HVAC system. |  |  |  | L/min | 3.785 |  |  |  | Enter the efficiency of all pumps ("pump efficiency" in this case refers to "pump mechanical efficiency") used on this service water heating system. When multiple pumps are present, define the capacity-weighted average efficiency for all the pumps. Value must be between 30% and 75%. | [5 empty] | Date of plans: |  | Date of plans: |  |  |  | Kamloops | Br. Columbia | 5
| Powered induction unit | 9 |  | ToV7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 |  | Return fan total static pressure |  | BaV7 | 4 | 4 | 1.3 | 2 | 4 | 3 | 4 | 3 | 6 | 4 | 3 | 4 | 4 | 2 | 2 | 2 | 2 | 2 | 6 | 6 | 6 | 1.3 | 2 | 6 | 2 | 2 | 2 | Oil-fired boilers, residulal (No.5 or No.6 oil) and other, >= 88 kW and < 733 kW | 83.4% | Et |  | Computer Room Air Conditioners |  |  | 6 | Airfoil with inlet vanes | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 | 0.366 |  | 1 | 8 | 8 | 0.0163 | -3.7735e-06 | 2.4165e-10 | -0.0016946 | 3.8904e-07 | -2.4707e-11 | HDD | Valeurs pour la série originale de coefficients | [5 empty] | RSI Value | 0.17612 | [5 empty] | French | English | Oil-fired, storage-type, <= 30.5 kW | 0.55 |  | Faucet flow ratio | [9 empty] | Enter the return fan design total static pressure. It is important not to enter the external static pressure value, sometimes indicated on the equipment specifications. |  |  |  | L/min | 3.785 |  |  |  | The installed recovery capacity divided by the total installed capacity of the SWH system, from the design specifications. If the heat recovery is limited to grey-water waste heat recovery then the installed recovery capacity is = Q * (Tin - Tout) * 4.182, where Q: flow rate (L/s), Tin: inlet temperature (warm) of the waste heat fluid (°C), Tout: outlet temperature (cold) of the waste heat fluid (°C). Value must be between 0 and 1. The conversion rate from litre per second to USGPM is 15.85 | [5 empty] | Building conditioned Floor area |  | Building conditioned Floor area |  |  |  | Toronto | Ontario | 5
| Built-up multi-zone system | 10 |  | ToV8 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 |  | Heating coil design temperature drop |  | BaV8 | 3.2932 | 3.2932 | 3.2932 | 3.2932 | 3.2932 | 3.2932 | 3.2932 | 3.2932 | 3.2932 | 3.2932 | 3.2932 | 3.2932 | 3.2932 | 3.29 | 3.29 | 3.29 | 3.29 | 3.29 | 3.2932 | 3.2932 | 3.2932 | 3.2932 | 3.29 | 3.2932 | 3.2932 | 3.2932 | 3.29 | Oil-fired boilers, residulal (No.5 or No.6 oil) and other, >= 733 kW | 85.8% | Ec |  | Packaged Water Chillers |  |  | 6 | Riding fan curve | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 |  | 1 | 9 | 9 | -0.077256 | 9.584e-06 | -3.2999e-10 | 0.0048486 | -1.1263e-06 | 6.5972e-11 | HDD | Montreal | 4682 | 519 | 5201 |  |  | Pa | 249.09 |  | Type de système de CVC : | System Type: |  |  | Oui | Yes | Oil-fired, storage-type, > 30.5 kW | 0.55 |  | Shower flow ratio | [9 empty] | Enter the design temperature differential for the HVAC system heating coil. If multiple coils are present, use the capacity-weighted average value. |  |  |  | % | 1 |  |  |  | Enter the average flow rate of all faucets served by the service water heating system. Value must be greater than 0.1 and smaller than 4 gpm (0.006309 and 15.14 L/min). | [5 empty] | Climate zone: |  | Building Location Heating Degree-Days: |  |  |  | Castlegar | Br. Columbia | 5 |  |  | Glossary |  | Glossaire
| Packaged multi-zone system | 11 |  | ToV9 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 |  | Baseboard heater design temperature drop |  | BaV9 | 1 | 1 | 0 | 0.6 | 1 | 0.6 | 1 | 0.6 | 1.5 | 1 | 0.6 | 1 | 1 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 1.5 | 1.5 | 1.5 | 0.6 | 0.6 | 1.5 | 0.6 | 0.6 | 0.6 | Gas-fired warm-air furnaces, <= 117.23 kW | 92.4% | AFUE |  |  |  |  | 15 | Dual DBT | 0.8 | 0.8 | 0.85 | 0.85 | 0.85 | 0.8 | 0.85 | 0.85 | 0.85 | 0.8 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 |  | 1 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | Toronto | 4176 | 533 | 4709 |  |  | °C | 0.55556 |  | Type primaire de système de refroidissement : | Cooling System Type: |  |  | Non | No |  |  |  | Average flow of other uses | [9 empty] | Enter the design temperature differential for the baseboard heaters. |  |  |  | % | 1 |  |  |  | Enter the average flow rate of all shower heads served by the service water heating system. Value must be greater than 0.1 and smaller than 4 gpm (0.006309 and 15.14 L/min). | [5 empty] | Building Location Cooling Degree-Days: |  | Building Location Cooling Degree-Days: |  |  |  | Victoria | Br. Columbia | 5 |  |  | English |  | français
| Constant-volume dual-duct system | 12 |  | ToV10 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Boiler/furnace/heat pump heating efficiency |  | BaV10 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | Gas-fired warm-air furnaces, > 117.23 kW | 81% | Et |  |  |  |  | 15 | Enthalpy | 0.80001 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 |  | 1 | 11 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | Halifax | 4240 | 304 | 4544 |  |  | °C | 0.55556 |  | Type secondaire de système de refroidissement : | Cooling Sub-System Type: | French | English | [15 empty] | Enter the heating equipment efficiency. For heat pumps, the COP must be expressed as fractions, such as 0.83 for 83% efficiency. For smaller equipment where only the AFUE is available, enter this value directly. If more than one piece of equipment is serving the system, enter the capacity-weighted average efficiency. If multiple energy sources are used, the fuel source of equipment providing the majority of the heating load must be selected. |  | French | English | L | 3.785 | Type de système : | System Type: |  | Define the typical weekly fraction of the hot water volume used by faucets through this service water heating system. Refer to standard calculation methods such as those presented in ASHRAE to evaluate this %. This value must be between 0% and 100%. |  | Conformité des systèmes de chauffage de l'eau sanitaire (CES) | Compliance of the service water heating (SWH) systems | Conformité des systèmes de chauffage, ventilation et conditionnement de l'air (CVCA) | Compliance of the heating, ventilating and air-conditioning systems (HVAC) | Number of HVAC Systems in the Building: |  | Number of SWH Systems in the Building: |  |  |  | Prince Rupert | Br. Columbia | 6
| Variable-volume dual-duct system | 13 |  | ToV11 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 |  | Chillers/direct expansion system/heat pump cooling efficiency |  | BaV11 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | Gas-fired duct furnaces, <= 117.23 kW | 81% | Et |  | Sub-System |  |  | 15 | Dual Enthalpy | 0.8005 | 0.80001 | 0.95 | 0.95 | 0.95 | 0.8 | 0.95 | 0.95 | 0.95 | 0.80004 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 |  | 1 | 12 | 12 | 0.77478 | 2.1285e-06 | 3.7633e-09 | 0 | 0 | 0 | HDD | Vancouver | 3157 | 220 | 3377 |  |  | Fraction | 1 |  | Puissance de refroidissement : | Cooling capacity: | Le système de CVCA est considéré conforme à la section 5.3 | HVAC system deemed to comply with Section 5.3 | [15 empty] | Enter the cooling equipment efficiency. All efficiencies have to be entered in terms of COP. If more than one piece of equipment is serving the system, enter the capacity-weighted average efficiency. |  | Le système de CES est considéré conforme à la section 6.3 | The SWH system is deemed to comply with Section 6.3 |  |  | Type d'appareil : | Equipment Type: |  | Define the typical weekly fraction of the hot water volume used by showers through this service water heating system. Refer to standard calculation methods such as those presented in ASHRAE to evaluate this %. This value must be between 0% and 100%. | [5 empty] | Overall HVAC-TOI: |  | Overall SWH-TOI: |  |  |  | Halifax | Nova Scotia | 6 |  |  | OA | Outdoor Air | AE | Air extérieur
| Two-pipe fan coil with optional make-up air unit | 14 |  | ToV12 | [28 empty] | Rejection fan input power ratio |  | BaV12 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 3.096 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.85 | 0.8 | 0.8 | Gas-fired unit heaters, <= 117.23 kW | 82% | Et |  | Split System <= 19 (65000) | 4.395 | SEER | 15 | Fixed | 0.76117 | 0.80072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 13 | 13 | 0.074364 | 3.2082e-06 | -1.108e-09 | -0.0044639 | -2.3342e-07 | 7.0258e-11 | HDD | Winnipeg | 6032 | 415 | 6447 |  |  | COP | 1 |  | Type de système de chauffage : | Heating System Type: | Le système de CVCA est considéré non conforme à la section 5.3 | HVAC system does not comply with Section 5.3 | [15 empty] | Enter the heat rejection equipment unitary fan power. This value represents the ratio of the total installed fan power of the equipment divided by its heat rejection capacity, expressed in the same unit. |  | Le système de CES est considéré non conforme à la section 6.3 | The SHW system does not comply with Section 6.3 |  |  | Volume du réservoir : | Tank Volume: |  | Enter the average flow rates of all other appliances using hot water in this system. A default value of 7.6 L/min (2 gpm) can be used if other design data is unavailable. This value must be greater between 0 and 378.5 L/min and (100 gpm). | [5 empty] | Number of Compliant Systems: |  | Number of Compliant Systems: |  |  |  | Yarmouth | Nova Scotia | 6 |  |  | SPVAC | Single Package Vertical Air Conditioner | CAVM | Conditionneurs d'air verticaux monoblocs | bar: 1 to 27
| Four-pipe fan coil with optional make-up air unit | 15 |  | ToV13 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 |  | Cooling by direct use of outdoor air (air economizer) |  | BaV13 | 5.2 | 5.2 | 2.9595 | 5.2 | 2.7778 | 2.7778 | 5.2 | 2.7778 | 5.2002 | 5.2 | 2.8 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 3.52 | 3.937 | 5.2 | 5.2 | 5.2 | 2.9595 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | Oil-fired warm-air furnaces, <= 66 kW | 84.5% | Et |  | Single-package systems <= 19 (65000) | 4.102 | SEER | 15 | Dry Bulb | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | 1 | 14 | 14 | 0.11209 | -0.00016605 | 1.652e-08 | -0.43222 | 0.00018843 | -1.5814e-08 | TDD | Yellowknife | 8642 | 141 | 8783 |  |  | W/W | 3.413 |  |  |  | Données d'entrée incomplètes | Incomplete data entry | [15 empty] | Select the type of air-side economizer used in this HVAC system. |  | Données d'entrée incomplètes | Incomplete data entry | [11 empty] | Number of non-Compliant Systems: |  | Number of non-Compliant Systems: |  |  |  | London | Ontario | 6 |  |  | SPVHP | Single Package Vertical Heat Pump | TVM | Themopompes verticales monoblocs
| Three-pipe fan coil with optional make-up air unit | 16 |  | ToV14 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 |  | Outdoor airflow control |  | BaV14 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | 0.015 | Oil-fired warm-air furnaces, > 66 kW | 81.3% | Et |  | All phases > 19 (65000) and < 73 (250000) | 2.8421 | EER | 16 | Fraction of hourly | 0.84348 | 0.80001 | 0 | 0 | 0.85 | 0.85 | 0.85 | 0.85 | 0.85 | 0.8 | 0.85 | 0.85 | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 15 | 15 | 99.5152 | -0.46855 | 0.00046015 | -63.6506 | 0.30513 | -0.00030307 | CDD | [6 empty] | Selection | 1 | [20 empty] | Select the type of outdoor air control used for this HVAC system (DCV = Demand control ventilation). | [14 empty] | Statement of Compliance |  | Statement of Compliance |  |  |  | Trenton | Ontario | 6 |  |  | PTHP | Packaged Terminal Heat Pump | CAIL | Conditionneurs d'air intégrées locales
| Water-loop heat pump with optional make-up air unit | 17 |  | ToV15 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 |  | Exhaust air heat-recovery efficiency |  | BaV15 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | Oil-fired duct furnaces or unit heaters | 81% | Et |  | Air conditioners, all phases, split and single package >= 19 kW and < 40 kW, electric resistance heating section | 3.28 | COP | 16 | DCV Return | 0.90911 | 0.85108 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.84931 | 0.9 | 0.9 | 0.9 | 0.26018 | 0.26018 | 0.26018 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.9 | 0.12 | 0.11724 | 0.9 | 0.9 | 0.9 |  | 1 | 16 | 16 | -1.162 | 2.1738e-05 | 6.8452e-09 | 1.2986 | -1.2103e-06 | -7.954e-09 | TDD | [6 empty] | Selection | 1 | [20 empty] | Enter the design heat recovery effectiveness. | [14 empty] | This Certificate of Compliance lists the Building features as per actual building permit drawings and specifications in accordance with Part 5.3 of the National Energy Code for Buildings. |  | This Certificate of Compliance lists the Building features as per actual building permit drawings and specifications in accordance with Part 6.3 of the National Energy Code for Buildings. |  |  |  | Montreal (Dorval) | Quebec | 6 |  |  | PTAC | Packaged Terminal Air Conditioner | TIL | Thermopompes intégrées locales
| Ground-source heat pump with optional make-up air unit | 18 |  | ToV16 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 |  | Cooling by indirect use of outdoor air (water economizer) |  | BaV16 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Air conditioners, all phases, split and single package >= 19 kW and < 40 kW, other heating section | 3.22 | COP | 16 | DCV Supply | 0.90593 | 0.85105 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.88 | 0.8493 | 0.88 | 0.88 | 0.88 | 0.24075 | 0.24075 | 0.24075 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.88 | 0.11 | 0.10883 | 0.88 | 0.88 | 0.88 |  | 1 | 17 | 17 | 0.026827 | -2.5286e-05 | 5.1761e-09 | -0.028839 | 2.113e-05 | -3.5018e-09 | TDD | [6 empty] | % | 1 | [10 empty] | Efficacité de l'équipement de chauffage de l'eau sanitaire | Service water heating equipment efficiency | Réservoir | Tank | [6 empty] | Enter the design water-side cooling coil heat exchange effectiveness. | [14 empty] | National Energy Code for Buildings |  | National Energy Code for Buildings |  |  |  | Greenwood | Nova Scotia | 6 |  |  | VSD | Variable Speed Drive | CVD | Contrôle de la ventilation selon la demande
| Induction unit, two-pipe | 19 |  | ToV17 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 |  | Piping insulation - hot water |  | BaV17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | Air conditioners, all phases, split and single package >= 40 kW and < 70 kW, electric resistance heating section | 3.22 | COP | 16 | DCV, fraction of hourly, Return | 0.92987 | 0.85108 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.84931 | 0.93 | 0.93 | 0.93 | 0.26015 | 0.26015 | 0.26015 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.93 | 0.12 | 0.11724 | 0.93 | 0.93 | 0.93 |  | 1 | 18 | 18 | -0.011932 | 8.378e-05 | -1.1966e-07 | 0.016237 | -2.1651e-05 | 2.748e-08 | CDD | [6 empty] | % | 1 | [10 empty] | Indice d'isolation du réservoir | Tank insulation value | Sans réservoir (instantanné) | Tankless (instantaneous) | [6 empty] | Enter the average piping insulation value. | [14 empty] | Documentation Author |  | Documentation Author |  |  |  | Terrace | Br. Columbia | 6 |  |  | DCV | Demand Control Ventilation | TTS | Température de thermomètre sec
| Induction unit, four-pipe | 20 |  | ToV18 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 |  | Piping insulation - chilled water |  | BaV18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420.2% | 420.2% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | French | English |  |  | Air conditioners, all phases, split and single package >= 40 kW and < 70 kW, other heating section | 3.16 | COP | 16 | Fixed | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 19 | 19 | 0.088391 | -2.0985e-05 | 1.3451e-09 | -0.0060714 | 1.4518e-06 | -9.1345e-11 | TDD | [6 empty] | RSI Value | 0.17612 | [10 empty] | Indice d'isolation des tuyauteries | Piping insulation value | Chaudière pour le chauffage des espaces | Space-heating boiler | [6 empty] | Enter the average piping insulation value. | [14 empty] | The Coordinating Professional hereby certifies that the proposed building design represented in the construction documents and modelled for this permit application are consistent with all other forms and worksheets, specifications, and other calculations submitted with this permit application. The proposed building, as designed, meets the requirements of the National Energy Code for Buildings. |  | The Coordinating Professional hereby certifies that the proposed building design represented in the construction documents and modelled for this permit application are consistent with all other forms and worksheets, specifications, and other calculations submitted with this permit application. The proposed building, as designed, meets the requirements of the National Energy Code for Buildings. |  |  |  | Ottawa | Ontario | 6 |  |  | DBT | Dry Bulb Temperature | VAIAL | Ventilateur à aubes inclées vers l’avant avec lames
| Induction unit, three-pipe | 21 |  | ToV19 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Piping pressure losses - hot water |  | BaV19 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | Chaudieres electriques | Electric boilers |  |  | Air conditioners, all phases, split and single package >= 70 kW and < 223 kW, electric resistance heating section | 2.93 | COP | 27 | Demand-only | 0.85549 | 0.79709 | 0.89131 | 0.89921 | 0.84728 | 0.79713 | 0.82523 | 0.842 | 0.84779 | 0.7818 | 0.77853 | 0.78158 | 0.80193 | 0.98574 | 0.95884 | 0.95884 | 0.96 | 0.96 | 0.8 | 1.02 | 1.02 | 0.94997 | 1.0719 | 1.0964 | 0.86513 | 0.86345 | 1.0719 |  | 1 | 20 | 20 | 2.7067e-05 | 5.5148e-06 | -7.0919e-09 | 7.6532e-06 | -2.8917e-07 | 3.2009e-10 | CDD | [6 empty] | RSI Value | 0.17612 | [10 empty] | Efficacité du moteur de la pompe | Pump motor efficiency | [8 empty] | Enter the total hydronic heating system pressure losses. In the case of multiple loops associated with a single HVAC system, enter the equivalent head calculated using the flow and head of each loop and expressed as an equivalent head for the loop having the largest flow rate. | [14 empty] | I hereby affirm that I am eligible, under the provisions of the authorities having jurisdiction, to sign this document as the person responsible for its preparation; and that I am licensed as a civil engineer, mechanical engineer, electrical engineer or architect. |  | I hereby affirm that I am eligible, under the provisions of the authorities having jurisdiction, to sign this document as the person responsible for its preparation; and that I am licensed as a civil engineer, mechanical engineer, electrical engineer or architect. |  |  |  | Charlottetown | P.E.I. | 6 |  |  | VAV | Variable Air Volume | VAPAL | Ventilateur à aubes à profil aérodynamique avec lames
| Packaged terminal AC - split | 22 |  | ToV20 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 |  | Piping pressure losses - chilled water |  | BaV20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | Chaudieres au gaz < 88 (300000) | Gas-fired boilers, < 88 kW |  |  | Air conditioners, all phases, split and single package >= 70 kW and < 223 kW, electric resistance heating section | 2.87 | COP | 27 | Standby | 0.79543 | 0.78485 | 0.78312 | 0.78156 | 0.78587 | 0.78339 | 0.79151 | 0.79036 | 0.78635 | 0.7818 | 0.77853 | 0.78158 | 0.79798 | 0.77154 | 0.77094 | 0.77094 | 0.77 | 0.77 | 0.62164 | 0.77 | 0.77 | 0.77543 | 0.78514 | 0.76654 | 0.79111 | 0.79121 | 0.78514 |  | 1 | 21 | 21 | -0.0001786 | -1.7419e-08 | 1.2819e-12 | 1.9485e-07 | -4.4861e-11 | 4.2018e-15 | HDD | [6 empty] | kPa | 2.989 | [10 empty] | Efficacité de la pompe | Pump efficiency | [8 empty] | Enter the total hydronic cooling system pressure losses. In the case of multiple loops associated with a single HVAC system, enter the equivalent head calculated using the flow and head of each loop and expressed as an equivalent head for the loop having the largest flow rate. | [14 empty] | I affirm that I am eligible to sign this document as the person responsible for its preparation; and for the following reason: |  | I affirm that I am eligible to sign this document as the person responsible for its preparation; and for the following reason: |  |  |  | St. Hubert | Quebec | 6 |  |  |  |  | VAPA | Ventilateur à aubes à profil aérodynamique
| Radiant (in-floor, ceiling) with optional make-up air unit | 23 |  | ToV21 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Pump mechanical efficiency - hot water |  | BaV21 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | Chaudieres au gaz >= 88 (300000) et < 733 (2500000) | Gas-fired boilers, >= 88 kW and < 733 kW |  |  | Air conditioners, all phases, split and single package >= 223 kW, electric resistance heating section | 2.84 | COP | 27 | Snap zone | 0.80663 | 0.78688 | 0.85173 | 0.85665 | 0.80261 | 0.78574 | 0.79914 | 0.80293 | 0.80212 | 0.84981 | 0.85102 | 0.84846 | 0.8009 | 0.90595 | 0.89393 | 0.89393 | 0.89 | 0.89 | 0.77434 | 0.88 | 0.88 | 0.88411 | 1.0089 | 0.89876 | 0.86834 | 0.86618 | 1.0089 |  | 1 | 22 | 22 | 4.4626e-05 | -1.3555e-06 | 1.6429e-09 | -1.6991e-08 | -7.2959e-10 | 1.2425e-12 | CDD | [6 empty] | kPa | 2.989 | [10 empty] | Coefficient de récupération de chaleur | Heat recovery ratio | [8 empty] | Enter the pump motor efficiency. When multiple pumps serve the system, use the power-weighted average pump efficiency. | [14 empty] | Coordinating Professional: |  | Coordinating Professional: |  |  |  | Lethbridge | Alberta | 6 |  |  |  |  | CVCA | Chauffage, ventilation et conditionement d'air
| Active chilled beams with optional make-up air unit | 24 |  | ToV22 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 |  | Pump mechanical efficiency - chilled water |  | BaV22 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 60 | 40 | 40 | 40 | 60 | 60 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | Chaudieres au gaz >= 733 (2500000) | Gas-fired boilers, >= 733 kW |  |  | Air conditioners, all phases, split and single package >= 223 kW, other heating section | 2.78 | COP | 27 | Scheduled | 0.79748 | 0.78543 | 0.7856 | 0.78436 | 0.78766 | 0.78406 | 0.79269 | 0.79209 | 0.79037 | 0.78605 | 0.78352 | 0.7859 | 0.79841 | 0.77503 | 0.77652 | 0.77652 | 0.78 | 0.78 | 0.62164 | 0.78 | 0.78 | 0.77886 | 0.78679 | 0.77101 | 0.79298 | 0.793 | 0.78679 |  | 1 | 23 | 23 | 0.04106 | 9.9307e-06 | -8.2825e-10 | -0.021567 | -6.0291e-06 | 5.1058e-10 | TDD | [6 empty] | % | 1 | [10 empty] | Débit moyen de l'ensembles des robinets | Average flow of all faucets | [8 empty] | Enter the pump motor efficiency. When multiple pumps serve the system, use the power-weighted average pump efficiency. | [14 empty] | Date: |  | Date: |  |  |  | Cranbrook | Br. Columbia | 6 |  |  |  |  | CA | Conditionnement d'air
| Unit heater | 25 |  | ToV23 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Pump motor efficiency - hot water |  | BaV23 | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | Chaudieres au mazout < 88 (300000) | Oil-fired boilers, < 88 kW |  |  | Heat Pumps >= 19 kW and < 40 kW, electric resistance heating section, split and single | 3.22 | COP | 27 | Snap outdoor | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | 1 | 24 | 24 | -0.01101 | 0.00030371 | -3.6644e-07 | 0.0068313 | -0.0001741 | 2.0938e-07 | CDD | [6 empty] | % | 1 | [10 empty] | Débit moyen de l'ensembles des douches | Average flow of all showers | [8 empty] | Enter the design efficiency of the pump motor. When multiple pumps serve the system, use the power-weighted average motor efficiency. | [14 empty] | Signature: |  | Signature: |  |  |  | Fredericton | New Brunswick | 6 |  |  |  |  | VAV | Volume d'air variable
| Unit ventilator | 26 |  | ToV24 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 |  | Pump motor efficiency - chilled water |  | BaV24 | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | 60% | Chaudieres au mazout >= 88 (300000) et < 733 (2500000) | Oil-fired boilers, >= 88 kW and < 733 kW |  |  | Heat Pumps >= 19 kW and < 40 kW, other heating section, split and single | 3.16 | COP | 28 | Demand-only | 0.80211 | 0.81651 | 0.74526 | 0.75937 | 0.80113 | 0.80113 | 0.0036904 | 0.80113 | 0.80113 | 0.812 | 0.80113 | 0.80955 | 0.8357 | 0.8 | 0.76858 | 0.76858 | 0.81 | 0.81 | 0.8 | 0.8 | 0.8 | 0.74526 | 0.8505 | 0.79014 | 0.75937 | 0.75937 | 0.8505 |  | 1 | 25 | 25 | 0.027826 | 7.041e-06 | -5.3517e-10 | -0.010491 | -2.6714e-06 | 1.989e-10 | HDD | [6 empty] | % | 1 | [10 empty] | Coefficient de débit des robinets | Faucet flow ratio | [8 empty] | Enter the design efficiency of the pump motor. When multiple pumps serve the system, use the power-weighted average motor efficiency. | [14 empty] | Check One |  | Check One |  |  |  | Truro | Nova Scotia | 6
| Radiation with optional make-up air unit | 27 |  | ToV25 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Hot water pump control |  | BaV25 | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | Chaudieres au mazout >= 733 (2500000) | Oil-fired boilers, >= 733 kW |  |  | Heat Pumps >= 40 kW and < 70 kW, electric resistance heating section, split and single | 3.1 | COP | 28 | Standby | 0.79241 | 0.8148 | 0.68748 | 0.72358 | 0.76265 | 0.76265 | -2.4819e-05 | 0.76265 | 0.76265 | 0.81089 | 0.76265 | 0.80841 | 0.8253 | 0.79605 | 0.76307 | 0.76307 | 0.8 | 0.8 | 0.62164 | 0.8 | 0.8 | 0.68748 | 0.77148 | 0.78934 | 0.72358 | 0.72358 | 0.77148 |  | 1 | 26 | 26 | -0.0037224 | 0.00015204 | -1.593e-07 | 0.0012069 | -5.5162e-05 | 5.2642e-08 | CDD | [6 empty] | % | 1 | [10 empty] | Coefficient de débit des douches | Shower flow ratio | [8 empty] | Select the hot water pump control logic applicable to this system. | [14 empty] | Summary compliance results |  | Summary compliance results |  |  |  | Summerside | P.E.I. | 6
|  |  |  | ToV26 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 |  | Chilled water pump control |  | BaV26 | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | 90% | Chaudieres au mazout residuel (#5 ou 6) et autres < 88 (300000) | Oil-fired boilers, residulal (No.5 or No.6 oil) and other, < 88 kW |  |  | Heat Pumps >= 40 kW and < 70 kW, otherheating section, split and single | 3.04 | COP | 28 | Snap zone | 0.80515 | 0.82308 | 0.71018 | 0.73547 | 0.77988 | 0.77988 | 0.0085289 | 0.77988 | 0.77988 | 0.81089 | 0.77988 | 0.80841 | 0.82713 | 0.77425 | 0.76511 | 0.76511 | 0.81 | 0.81 | 0.75884 | 0.8 | 0.8 | 0.71018 | 0.77361 | 0.79068 | 0.73547 | 0.73547 | 0.77361 |  | 1 | 27 | 27 | -131.4748 | 0.048216 | -3.9042e-06 | 79.7918 | -0.028984 | 2.3417e-06 | HDD | [6 empty] | Selection | 1 | [10 empty] | Débit moyen de tous les autres usages | Average flow of other uses | [8 empty] | Select the chilled water pump control logic applicable to this system. | [14 empty] | National Energy Code of Canada for Buildings – 2011 |  | National Energy Code of Canada for Buildings – 2011 |  |  |  | Medicine Hat | Alberta | 6
|  |  |  | ToV27 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Hot water loop temperature control |  | BaV27 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | Chaudieres au mazout residuel (#5 ou 6) et autres >= 88 (300000) et < 733 (2500000) | Oil-fired boilers, residulal (No.5 or No.6 oil) and other, >= 88 kW and < 733 kW |  |  | Heat Pumps >= 70 kW, electric resistance heating section, split and single | 2.78 | COP | 28 | Scheduled | 0.80263 | 0.82025 | 0.75491 | 0.79127 | 0.77311 | 0.77311 | 0.0051459 | 0.77311 | 0.77311 | 0.81584 | 0.77311 | 0.81346 | 0.83409 | 0.8 | 0.75062 | 0.75062 | 0.81 | 0.81 | 0.62164 | 0.79 | 0.79 | 0.75491 | 0.75339 | 0.78615 | 0.79127 | 0.79127 | 0.75339 |  | 1 | 28 | 28 | -0.21746 | 0.00016105 | -1.9762e-08 | 1.0814 | -0.00034476 | 2.8874e-08 | CDD | [6 empty] | Selection | 1 | [20 empty] | Select the hot water temperature control logic applicable to this system. | [14 empty] | 0 |  | 0 |  |  |  | Moncton | New Brunswick | 6
|  |  |  | ToV28 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 |  | Chilled water loop temperature control |  | BaV28 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | Chaudieres au mazout residuel (#5 ou 6) et autres >= 88 (300000) et < 733 (2500000) | Oil-fired boilers, residulal (No.5 or No.6 oil) and other, >= 733 kW |  |  | Heat Pumps >= 70 kW, other heating section, split and single | 2.72 | COP | 28 | Snap outdoor | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | 1 | 29 | 29 | 40.9117 | -0.01309 | 9.2719e-07 | -23.1669 | 0.0076326 | -5.4418e-07 | HDD | [6 empty] | Selection | 1 | [20 empty] | Select the chilled water temperature control logic applicable to this system. | [20 empty] | Mount Forest | Ontario | 6
| French | English |  | ToV29 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | Hot water flow control |  | BaV29 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | Generateurs d'air chaud au gaz <= 117.23 (400000) | Gas-fired warm-air furnaces, <= 117.23 kW |  |  | Heat Pumps >= 19 kW and < 70 kW in cooling mode at 8.3 ⁰C db / 6.1 ⁰C wb | 3.3 | COP | 29 | Fixed | 0.79142 | 0.79903 | 0.78308 | 0.7821 | 0.79446 | 0.79446 | 0.79446 | 0.79446 | 0.79446 | 0.79946 | 0.79446 | 0.79446 | 0.79131 | 0.79075 | 0.76656 | 0.76656 | 0.77 | 0.77 | 0.7792 | 0.79 | 0.79 | 0.78308 | 0.76656 | 0.79106 | 0.62004 | 0.61885 | 0.76656 |  | 1 | 30 | 30 | -5.6007 | 0.013251 | 1.2808e-05 | 3.552 | -0.004414 | -1.3427e-05 | CDD | [6 empty] | Selection | 1 | [7 empty] | Électrique | Electric | 0.98 | [10 empty] | Select the hot water pump flow control applicable to this system. In the case where multiple pumps used different controls, select the type that controls the majority of the pump installed power. | [20 empty] | Saint John | New Brunswick | 6
1 | À blocs autonomes à volume variable | Built-up variable-volume |  | ToV30 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 |  | Chilled water flow control |  | BaV30 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | Generateurs d'air chaud au gaz > 117.23 (400000) | Gas-fired warm-air furnaces, > 117.23 kW |  |  | Heat Pumps >= 19 kW and < 70 kW in cooling mode at 8.3 ⁰C db / -9.4 ⁰C wb | 2.25 | COP | 29 | Scheduled | 0.7974 | 0.79958 | 0.7958 | 0.79541 | 0.79821 | 0.79821 | 0.79821 | 0.79821 | 0.79821 | 0.79994 | 0.79821 | 0.79821 | 0.79851 | 0.79784 | 0.76858 | 0.76858 | 0.77 | 0.77 | 0.79122 | 0.8 | 0.8 | 0.7958 | 0.7938 | 0.79728 | 0.74332 | 0.73724 | 0.7938 |  | 1 | 31 | 31 | -133.6625 | 0.05146 | -4.3932e-06 | 83.2734 | -0.031825 | 2.7173e-06 | TDD | [6 empty] | Selection | 1 | [7 empty] | Chauffe-eau avec thermopompe | Heat pump water heaters | 2.1 | EF | [9 empty] | Select the chilled water pump flow control applicable to this system. In the case where multiple pumps used different controls, select the type that controls the majority of the pump installed power. | [11 empty] | Statement of Compliance – National Energy Code of Canada for Buildings 2011 |  |  | Déclaration de conformité – Code national de lénergie pour les bâtiments – Canada 2011 Rapport sommaire de conformité à la partie 5 du NECB - CVCA | Statement of Compliance – National Energy Code of Canada for Buildings 2011 Summary Compliance Report to NECB Part 5 - HVAC | Déclaration de conformité – Code national de lénergie pour les bâtiments – Canada 2011 Rapport sommaire de conformité à la partie 6 du NECB - CES | Statement of Compliance – National Energy Code of Canada for Buildings 2011 Summary Compliance Report to NECB Part 6 - SWH |  |  | St John's | Newfoundland | 6
2 | Réchauffage à volume constant | Constant-volume reheat |  | ToV31 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  |  |  | BaV31 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5 | Generateurs d'air chaud de conduit au gaz <= 117.23 (400000) | Gas-fired duct furnaces, <= 117.23 kW |  |  | Heat Pumps >= 70 kW in cooling mode at 8.3 ⁰C db / 6.1 ⁰C wb | 3.2 | COP | 29 | Load reset | 0.86746 | 0.81539 | 0.90771 | 0.91766 | 0.8544 | 0.8544 | 0.8544 | 0.8544 | 0.8544 | 0.80076 | 0.8544 | 0.8544 | 0.83112 | 1.0477 | 1.0298 | 1.0298 | 1.03 | 1.03 | 0.84526 | 1.05 | 1.05 | 0.90771 | 1.0405 | 1.1301 | 1.2211 | 1.2297 | 1.0405 |  | 1 | 32 | 32 | -2.4991 | 0.032644 | -5.4833e-05 | 1.4812 | -0.016384 | 2.9382e-05 | CDD | [6 empty] | Selection | 1 | [7 empty] | Au gaz < 22 kW | Gas-fired < 22 kW | -1 | EF = 0.67 - 0.0005V | [9 empty] | Choose from the list of 27 HVAC System Types ID available in the drop down list and as provided in Table 5.3.1.1 of the NECB. The components that are applicable to the system will then be visible. In all instances where a visible component is NOT part of the system being evaluated, its value must be defined as identical to that of the Reference value for a compliance calculation. | [8 empty] | Tableau d'aide pour le CES | SWH Help Table |  |  |  |  | Nom du projet : | Project Name: | Nom du projet : | Project Name: |  |  | Sherbrooke | Quebec | 6
3 | Intégrée à un conduit - monozone | Packaged single duct - single zone |  | ToV32 | 1 | 1 | 0 | 1 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 |  |  |  | BaV32 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | Generateurs de chaleur suspendus au gaz <= 117.23 (400000) | Gas-fired unit heaters, <= 117.23 kW |  |  | Heat Pumps >= 70 kW in cooling mode at 8.3 ⁰C db / -9.4 ⁰C wb | 2.05 | COP | 29 | OA Reset, min 140 °F | 0.79956 | 0.79991 | 0.79945 | 0.7994 | 0.79979 | 0.79979 | 0.79979 | 0.79979 | 0.79979 | 0.79998 | 0.79979 | 0.79979 | 0.80005 | 0.79927 | 0.78996 | 0.78996 | 0.79 | 0.79 | 0.79753 | 0.8 | 0.8 | 0.79945 | 0.79947 | 0.7993 | 0.79239 | 0.79047 | 0.79947 |  | 2 | 1 | 33 | 0.10555 | 6.4719e-05 | -4.6329e-09 | -0.054979 | -3.4641e-05 | 2.4268e-09 | HDD | [6 empty] | W | 1 | [7 empty] | Au gaz 22 - 117 kW | Gas-fired 22 - 117 kW | -2 | EF = 0.67 - 0.0005V | [9 empty] | Choose the type of cooling equipment associated with this HVAC system as defined in Table 5.2.12.1 of the NECB. | [7 empty] | Type de système : | Sélectionner le type de système qui correspond le mieux à celui à être évalué. | Select the system type that most closely matches the one being evaluated. |  |  |  |  | Addresse du projet : | Project Address: | Addresse du projet : | Project Address: |  |  | Stephenville | Newfoundland | 6
4 | À blocs autonomes à un conduit - monozone | Built-up single duct - single zone | [60 empty] | Generateurs d'air chaud au mazout <= 66 (225000) | Oil-fired warm-air furnaces, <= 66 kW |  |  | SPVAC and SPVHP in cooling mode < 19 kW | 2.93 | EER | 29 | OA Reset, min >140 °F | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | 2 | 2 | 34 | 0.081632 | 4.2145e-05 | -3.0264e-09 | -0.032387 | -1.5624e-05 | 1.0972e-09 | HDD | [15 empty] | Au gaz > 117 kW | Gas-fired > 117 kW | 0.77 | Et | [9 empty] | Choose the precise category associated with the cooling equipment system type, as defined in Table 5.2.12.1 of the NECB. |  |  |  | French | English |  |  | Type d'appareil : | Sélectionner le type d'appareil servant à produire l'eau chaude sanitaire. | Select the type of equipment used in producing the service hot water. |  |  |  |  | Nom du soumissionaire : | Applicant Name: | Nom du soumissionaire : | Applicant Name: |  |  | Williams Lake | Br. Columbia | 7A
5 | Intégrée à volume variable | Packaged variable-volume | [60 empty] | Generateurs d'air chaud au mazout <= 66 (225000) | Oil-fired warm-air furnaces, > 66 kW |  |  | SPVAC and SPVHP in cooling mode >= 19 kW and < 40 kW | 2.7835 | EER | 30 | Fixed | 0.77744 | 0.79399 | 0.76797 | 0.76057 | 0.80354 | 0.80354 | 0.78295 | 0.79516 | 0.76929 | 0.79656 | 0.80354 | 0.80354 | 0.77572 | 0.8 | 0.77344 | 0.77344 | 0.8 | 0.8 | 0.8 | 0.78 | 0.78 | 0.76797 | 0.78415 | 0.78342 | 0.76057 | 0.76057 | 0.78415 |  | 2 | 3 | 35 | -0.049402 | 0.00010791 | -7.3748e-09 | 0.041751 | -9.4377e-05 | 6.4241e-09 | HDD | [6 empty] | French | English | [7 empty] | Au mazout, instantanné, <= 61.5 kW | Oil-fired, instantaneous, <= 61.5 kW | -3 | EF = 0.59 - 0.0019V | [9 empty] | This value only serves in defining the Reference value performance for certain type of cooling equipment, as defined in Table 5.2.12.1 of the NECB. |  |  |  | % | % |  |  | Volume du réservoir : | Volume total de tous les réservoirs associés à ce système. La valeur doit être égale ou supérieure à 0. | Total volume of all storage tanks included in this system. Value must be equal or greater than 0. |  |  |  |  | Adresse du soumissionaire : | Applicant Address: | Adresse du soumissionaire : | Applicant Address: |  |  | Sault Ste. Marie | Ontario | 7A
6 | Intégrée à volume constant avec réchauffage | Packaged constant-volume with reheat | [60 empty] | Generateur de chaleur suspendus et generateurs d'air chaud de conduit au mazout | Oil-fired duct furnaces or unit heaters |  |  | SPVAC and SPVHP in cooling mode >= 40 kW and < 70 kW | 2.5198 | EER | 30 | Scheduled | 0.78839 | 0.79673 | 0.77958 | 0.77397 | 0.8 | 0.8 | 0.79105 | 0.79791 | 0.78341 | 0.79812 | 0.8 | 0.8 | 0.78758 | 0.80403 | 0.78681 | 0.78681 | 0.84 | 0.8 | 0.80198 | 0.79 | 0.79 | 0.77958 | 0.79294 | 0.79115 | 0.77397 | 0.77397 | 0.79294 |  | 2 | 4 | 36 | -0.02366 | 5.1179e-05 | -3.4982e-09 | 0.0099023 | -2.2291e-05 | 1.5164e-09 | HDD | [6 empty] | % | % | [7 empty] | Au mazout, instantanné, Vt < 37.8 L | Oil-fired, instantaneous, Vt < 37.8 L | 0.8 | Et | [9 empty] | Choose the type of heating equipment associated with this HVAC system as defined in Table 5.2.12.1 of the NECB. For all resistance electric heating cases, the user must select "Electric boilers". However, in this case, all of the components relating to the hot water distribution system must be defined using the Reference values. |  |  |  | Valeur RSI | RSI Value |  |  | Efficacité de l'équipement de chauffage de l'eau sanitaire | Entrer le rendement de l'équipement servant à produire l'eau chaude sanitaire. Pour les pompes à chaleur, le COP doit être défini en terme de %. Dans le cas des facteurs d'efficacité (EF), utiliser directement cette valeur, sauf pour les chauffe-eau électriques où un efficacité de 100% doit être utilisé. Si plus d'un appareil du même type est associé au système, définir le rendement pondéré selon la puissance des appareils. La valeur doit être supérieure à 0. | Enter the efficiency of the equipment used in producing the service hot water. For heat pumps, enter the COP in terms of %. For Efficiency Factors (EF), enter directly that value except for electric hot water tanks where an efficiency of 100% is to be used. If more than one equipment of the same type serves a system, enter the capacity-weighted average efficiency. Value must be greater than 0. |  |  |  |  | Téléphone du soumissionaire : | Applicant Phone: | Téléphone du soumissionaire : | Applicant Phone: |  |  | Calgary | Alberta | 7A
7 | À blocs autonomes à VAV et dérivation au plafond | Built-up ceiling bypass VAV | [64 empty] | SPVHP in heating mode < 19 kW | 3.1 | COP | 30 | Load reset | 0.8333 | 0.808 | 0.79419 | 0.80139 | 0.80354 | 0.80354 | 0.82663 | 0.85575 | 0.83598 | 0.8041 | 0.80354 | 0.80354 | 0.83242 | 0.82226 | 0.84046 | 0.84046 | 0.8 | 0.8 | 0.80064 | 0.8 | 0.8 | 0.79419 | 0.82177 | 0.80065 | 0.80139 | 0.80139 | 0.82177 |  | 2 | 5 | 37 | -7.3001 | 0.0027086 | -1.9047e-07 | 13.4103 | -0.0043904 | 3.1019e-07 | HDD | [6 empty] | % | % | [7 empty] | Au mazout, instantanné, Vt >= 37.8 L | Oil-fired, instantaneous, Vt >= 37.8 L | 0.77 | Et | [13 empty] | Valeur RSI | RSI Value |  |  | Indice d'isolation du réservoir | Spécifier le niveau d'isolation du réservoir. Dans le cas où plusieurs réservoirs sont présents, définir la valeur d'isolation pondérée selon la surface des réservoirs. La valeur doit être entre R0.1 et 40 (RSI 0.5678-7.04). | Define the tank's insulating value. For systems with multiple tanks, enter the surface-weighted average insulating value. Value must be between R 0.1 and 40 (RSI 0.5678-7.04). |  |  |  |  | Information général | General information | Information général | General information |  |  | Gander | Newfoundland | 7A
8 | Intégrée à VAV et dérivation au plafond | Packaged ceiling bypass VAV | [64 empty] | SPVHP in heating mode >= 19 kW and < 40 kW | 3 | COP | 30 | OA Reset, min 58 °F | 0.81697 | 0.80434 | 0.81361 | 0.81676 | 0.80354 | 0.80354 | 0.81254 | 0.79949 | 0.82235 | 0.80243 | 0.80354 | 0.80354 | 0.81819 | 0.81694 | 0.81731 | 0.81731 | 0.84 | 0.8 | 0.80278 | 0.81 | 0.81 | 0.81361 | 0.80745 | 0.81362 | 0.81676 | 0.81676 | 0.80745 |  | 2 | 6 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [6 empty] | % | % | [7 empty] | Au mazout, à accumulation, <= 30.5 kW | Oil-fired, storage-type, <= 30.5 kW | 0.55 | EF | [13 empty] | % | % |  |  | Indice d'isolation des tuyauteries | Spécifier le niveau d'isolation moyen de l'ensemble de la tuyauterie du système d'eau chaude sanitaire. La valeur doit être entre R0.1 et 40 (RSI 0.5678-7.04). | Define the average piping insulation value for this service water heating system. Value must be between R 0.1 and 40 (RSI 0.5678-7.04). |  |  |  |  | Date des plans : | Date of plans: | Date des plans : | Date of plans: |  |  | Quebec | Quebec | 7A
9 | Éjecto-convecteur assisté | Powered induction unit | [64 empty] | SPVHP in heating mode >= 40 kW and < 70 kW | 2.9 | COP | 30 | OA Reset, min <54 °F | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 |  | 2 | 7 | 39 | -0.0056467 | -3.9776e-06 | 3.1101e-10 | 0.00013974 | 1.2214e-07 | -1.1937e-11 | TDD | [6 empty] | % | % | [7 empty] | Au mazout, à accumulation, > 30.5 kW | Oil-fired, storage-type, > 30.5 kW | 0.55 | EF | [13 empty] | % | % |  |  | Efficacité du moteur de la pompe | Entrer l'efficacité du moteur de la pompe de circulation du système d'eau chaude sanitaire. Si plusieurs pompes sont présentes, définir l'efficacité moyenne pondérée selon la puissance des moteurs. La valeur doit être entre 30% et 99%. | Enter the efficiency of all pump motors used on this service water heating system. When multiple pumps are present, define the capacity-weighted average efficiency for all the pump motors. Value must be between 30% and 99%. |  |  |  |  | Superficie de plancher des zones climatisées | Building conditioned Floor area | Superficie de plancher des zones climatisées | Building conditioned Floor area |  |  | Prince George | Br. Columbia | 7A
10 | Système multizone constitué de blocs autonomes | Built-up multi-zone system | [64 empty] | Evaporatively cooled <= 19 (65000) | 3.54 | COP | 31 | VSD, valve reset | 0.81234 | 0.80338 | 0.51973 | 0.51311 | 0.51138 | 0.50395 | 0.50709 | 0.51017 | 0.50268 | 0.8016 | 0.50455 | 0.50163 | 0.51014 | 0.51805 | 0.51789 | 0.51789 | 0.5 | 0.5 | 0.52111 | 0.50951 | 0.50951 | 0.5174 | 0.51041 | 0.51172 | 0.58102 | 0.8795 | 0.51041 | x | 2 | 8 | 40 | -0.004605 | 8.683e-06 | 1.0549e-09 | 0.00028402 | -1.4343e-07 | 2.357e-11 | HDD | [6 empty] | Sélection | Selection | [24 empty] | W/W | W/W |  |  | Efficacité de la pompe | Entrer l'efficacité de la pompe de circulation du système d'eau chaude sanitaire. Si plusieurs pompes sont présentes, définir l'efficacité moyenne pondérée selon la puissance des pompes. La valeur doit être entre 30% et 75%. | Enter the efficiency of all pumps ("pump efficiency" in this case refers to "pump mechanical efficiency") used on this service water heating system. When multiple pumps are present, define the capacity-weighted average efficiency for all the pumps. Value must be between 30% and 75%. |  |  |  |  | Zone climatique du bâtiment : | Climate zone: | Degrés-jours de chauffage au lieu du bâtiment : | Building Location Heating Degree-Days: |  |  | North Bay | Ontario | 7A
11 | Système multizone intégré | Packaged multi-zone system | [64 empty] | Evaporatively cooled and water evaporatively cooled, split and single-package >= 19 kW and < 40 kW electric resistance heating section | 3.37 | COP | 31 | Two speed, .67 | 0.811 | 0.80264 | 0.51827 | 0.51186 | 0.51017 | 0.50329 | 0.50628 | 0.50919 | 0.50203 | 0.80107 | 0.50409 | 0.5011 | 0.50895 | 0.51502 | 0.51426 | 0.51426 | 0.5 | 0.5 | 0.51674 | 0.50761 | 0.50761 | 0.51624 | 0.50816 | 0.50937 | 0.57326 | 0.87177 | 0.50816 |  | 2 | 9 | 41 | 0.0081066 | -1.2719e-05 | 8.6054e-10 | -0.00046234 | 7.4347e-07 | -6.3126e-11 | TDD | [6 empty] | Sélection | Selection | [24 empty] | L/min | L/min |  |  | Coefficient de récupération de chaleur | La puissance de récupération installée divisée par la puissance installée totale de chauffage de l'eau sanitaire, d'après les spécifications de conception. Si la récupération est limitée à la récupération de chaleur des eaux grises, alors la puissance installée est = Q * (Tin - Tout) * 4.182, où Q: débit en L/s, Tin: température d'admission (chaude) du fluide de récupération (°C), Tout: température de sortie (froide) du fluide de récupération (°C). La valeur doit être entre 0 et 1. Le facteur de conversion des litres par seconde en gallons US par minute est 15,85. | The installed recovery capacity divided by the total installed capacity of the SWH system, from the design specifications. If the heat recovery is limited to grey-water waste heat recovery then the installed recovery capacity is = Q * (Tin - Tout) * 4.182, where Q: flow rate (L/s), Tin: inlet temperature (warm) of the waste heat fluid (°C), Tout: outlet temperature (cold) of the waste heat fluid (°C). Value must be between 0 and 1. The conversion rate from litre per second to USGPM is 15.85 |  |  |  |  | Degrés-jours de refroidissement au lieu du bâtiment : | Building Location Cooling Degree-Days: | Degrés-jours de refroidissement au lieu du bâtiment : | Building Location Cooling Degree-Days: |  |  | Edmonton | Alberta | 7A
12 | Système à deux conduits à volume constant | Constant-volume dual-duct system | [64 empty] | Evaporatively cooled and water evaporatively cooled, split and single-package >= 19 kW and < 40 kW other heating section | 3.31 | COP | 31 | VSD, fixed | 0.81223 | 0.80336 | 0.5197 | 0.51302 | 0.5113 | 0.50393 | 0.50701 | 0.51013 | 0.50262 | 0.80158 | 0.50453 | 0.50161 | 0.50989 | 0.51805 | 0.51789 | 0.51789 | 0.5 | 0.5 | 0.52001 | 0.50951 | 0.50951 | 0.51737 | 0.51029 | 0.51171 | 0.58102 | 0.87949 | 0.51029 |  | 2 | 10 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [6 empty] | Pa | Pa | [20 empty] | Tableau d'aide pour le CVCA | HVAC Help Table |  |  | L/min | L/min |  |  | Débit moyen de l'ensembles des robinets | Entrer le débit moyen de tous les robinets desservis par ce système d'eau chaude sanitaire. La valeur doit être supérieure à 0.1 mais inférieure à 4 gpm (0.006309 et 15.4 L/min). | Enter the average flow rate of all faucets served by the service water heating system. Value must be greater than 0.1 and smaller than 4 gpm (0.006309 and 15.14 L/min). |  |  |  |  | Nombre de systèmes de CVCA dans le bâtiment : | Number of HVAC Systems in the Building: | Nombre de systèmes de CES dans le bâtiment : | Number of SWH Systems in the Building: |  |  | Sudbury | Ontario | 7A
13 | Système à deux conduits à volume variable | Variable-volume dual-duct system | [30 empty] | French | English | [32 empty] | Evaporatively cooled and water evaporatively cooled, split and single-package >= 40 kW and < 70 kW electric resistance heating section | 3.22 | COP | 31 | Two speed, .5 | 0.81131 | 0.8027 | 0.51967 | 0.51255 | 0.5105 | 0.50313 | 0.50637 | 0.50984 | 0.50201 | 0.80112 | 0.50362 | 0.50113 | 0.50862 | 0.51827 | 0.51816 | 0.51816 | 0.5 | 0.5 | 0.51708 | 0.50962 | 0.50962 | 0.51742 | 0.50936 | 0.51187 | 0.58171 | 0.88011 | 0.50936 |  | 2 | 11 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [6 empty] | Valeur RSI | RSI Value | [13 empty] | Efficacité mécanique du ventilateur d'alimentation | [5 empty] | Supply fan mechanical efficiency | Entrer le rendement mécanique de conception du ventilateur d'alimentation. | Enter the supply fan design mechanical efficiency. |  |  | L/min | L/min |  |  | Débit moyen de l'ensembles des douches | Entrer le débit moyen de toutes les pommes de douches desservies par ce système d'eau chaude sanitaire. La valeur doit être supérieure à 0.1 mais inférieure à 4 gpm (0.006309 et 15.4 L/min). | Enter the average flow rate of all shower heads served by the service water heating system. Value must be greater than 0.1 and smaller than 4 gpm (0.006309 and 15.14 L/min). |  |  |  |  | Coefficient global HVAC-TOI : | Overall HVAC-TOI: | Coefficient global SWH-TOI : | Overall SWH-TOI: |  |  | Estevan | Saskatchewan | 7A
14 | Ventilo-convecteur à deux tuyaux avec unité d'appoint facultative | Two-pipe fan coil with optional make-up air unit | [29 empty] | ToV1 | Efficacité mécanique du ventilateur d'alimentation | Supply fan mechanical efficiency | [32 empty] | Evaporatively cooled and water evaporatively cooled, split and single-package >= 40 kW and < 70 kW other heating section | 3.16 | COP | 31 | Constant | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5 |  | 2 | 12 | 44 | 0.13158 | 6.8807e-05 | -1.5103e-09 | 0 | 0 | 0 | HDD | [6 empty] | Pa | Pa | [13 empty] | Efficacité du moteur d'alimentation | [5 empty] | Supply motor efficiency | Entrer le rendement de conception du moteur du ventilateur d'alimentation. | Enter the supply fan motor design efficiency. |  |  | % | % |  |  | Débit moyen de tous les autres usages | Définir la fraction du volume hebdomadaire typique d'eau chaude qui est attribuable aux robinets. Se référer à des méthodes telles celles de l'ASHRAE pour évaluer ce %. La valeur doit être entre 0% et 100%. | Define the typical weekly fraction of the hot water volume used by faucets through this service water heating system. Refer to standard calculation methods such as those presented in ASHRAE to evaluate this %. This value must be between 0% and 100%. |  |  |  |  | Nombre de systèmes conformes : | Number of Compliant Systems: | Nombre de systèmes conformes : | Number of Compliant Systems: |  |  | Swift Current | Saskatchewan | 7A
15 | Ventilo-convecteur à quatre tuyaux avec unité d'appoint facultative | Four-pipe fan coil with optional make-up air unit | [29 empty] | ToV2 | Efficacité du moteur d'alimentation | Supply motor efficiency | [32 empty] | Water evaporatively cooled air conditioners, split and single-packaged >= 70 kW electric resistance heating section | 3.22 | COP | 32 | VSD, valve reset | 0.80684 | 0.80165 | 0.8623 | 0.56038 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.80086 | 0.9 | 0.50085 | 0.50753 | 0.51892 | 0.50668 | 0.50668 | 0.54422 | 0.52 | 0.9 | 0.9 | 0.9 | 0.8623 | 0.51009 | 0.50359 | 0.56038 | 0.86038 | 0.51009 |  | 2 | 13 | 45 | 0.00012215 | 8.3228e-05 | -8.0258e-08 | -1.56e-05 | -5.2084e-06 | 5.0466e-09 | CDD | [6 empty] | °C | °C | ° | [12 empty] | Efficacité mécanique du ventilateur de reprise | [5 empty] | Return fan mechanical efficiency | Entrer le rendement mécanique de conception du ventilateur de reprise. | Enter the return fan design mechanical efficiency. |  |  | % | % |  |  | Coefficient de débit des robinets | Définir la fraction du volume hebdomadaire typique d'eau chaude qui est attribuable aux douches. Se référer à des méthodes telles celles de l'ASHRAE pour évaluer ce %. La valeur doit être entre 0% et 100%. | Define the typical weekly fraction of the hot water volume used by showers through this service water heating system. Refer to standard calculation methods such as those presented in ASHRAE to evaluate this %. This value must be between 0% and 100%. |  |  |  |  | Nombre de systèmes non conformes : | Number of non-Compliant Systems: | Nombre de systèmes non conformes : | Number of non-Compliant Systems: |  |  | Mont Joli | Quebec | 7A
16 | Ventilo-convecteur à trois tuyaux avec unité d'appoint facultative | Three-pipe fan coil with optional make-up air unit | [29 empty] | ToV3 | Efficacité mécanique du ventilateur de reprise | Return fan mechanical efficiency | [32 empty] | Water evaporatively cooled air conditioners, split and single-packaged >= 70 kW other heating section | 3.16 | COP | 32 | Two speed, .67, valve reset | 0.80526 | 0.80125 | 0.85932 | 0.55771 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.80064 | 0.8 | 0.50061 | 0.50549 | 0.51504 | 0.50517 | 0.50517 | 0.5 | 0.5 | 0.8 | 0.8 | 0.8 | 0.85932 | 0.50924 | 0.50182 | 0.55771 | 0.85771 | 0.50924 |  | 2 | 14 | 46 | 0.01106 | -0.00041604 | 3.7805e-07 | -0.055147 | 0.0003455 | -5.0377e-07 | CDD | [6 empty] | °C | °C | [13 empty] | Efficacité du moteur de reprise | [5 empty] | Return fan motor efficiency | Entrer le rendement de conception du moteur du ventilateur de reprise. | Enter the return fan motor design efficiency. |  |  | L | L |  |  | Coefficient de débit des douches | Entrer le débit moyen des autres appareils desservis par ce système d'eau chaude sanitaire. Une valeur de 7.6 L/min (2 gpm) peut être utilisée si aucune valeur de conception n'est disponible. La valeur doit être entre 0 et 378.5 L/min (100 gpm). | Enter the average flow rates of all other appliances using hot water in this system. A default value of 7.6 L/min (2 gpm) can be used if other design data is unavailable. This value must be greater between 0 and 378.5 L/min and (100 gpm). |  |  |  |  | Déclaration de conformité | Statement of Compliance | Déclaration de conformité | Statement of Compliance |  |  | Charlo (Campbellton) | New Brunswick | 7A
17 | Thermopompe sur boucle d'eau avec unité d'air d'appoint facultative | Water-loop heat pump with optional make-up air unit | [29 empty] | ToV4 | Efficacité du moteur de reprise | Return fan motor efficiency | [32 empty] | Air conditioner, air-cooled, electric or no heating - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, >=19 <40 kW | 3.2816 |  | 32 | VSD, fixed | 0.80223 | 0.80054 | 0.85443 | 0.55334 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.80029 | 0.7 | 0.50028 | 0.50254 | 0.51805 | 0.50246 | 0.50246 | 0.50581 | 0.49 | 0.7 | 0.7 | 0.7 | 0.85443 | 0.50764 | 0.50145 | 0.55334 | 0.85334 | 0.50764 |  | 2 | 15 | 47 | 0.040471 | -0.00011141 | 1.153e-07 | -0.02852 | 0.00011208 | -1.2837e-07 | CDD | [6 empty] | Fraction | Fraction | [13 empty] | Régulation de la température d'alimentation | [5 empty] | Supply temperature control | Choisir dans la liste déroulant le type de contrôle de température d'alimentation utilisé pour ce système de CVCA. | Choose from the drop down list the type of supply temperature control applicable to this HVAC system. | [13 empty] | Ce certificat de conformité énumère les caractéristiques du bâtiment selon les dessins et devis soumis pour le permis de construction selon la partie 5.3 du Code national de l’énergie pour les bâtiments | This Certificate of Compliance lists the Building features as per actual building permit drawings and specifications in accordance with Part 5.3 of the National Energy Code for Buildings. | Ce certificat de conformité énumère les caractéristiques du bâtiment selon les dessins et devis soumis pour le permis de construction selon la partie 6.3 du Code national de l’énergie pour les bâtiments | This Certificate of Compliance lists the Building features as per actual building permit drawings and specifications in accordance with Part 6.3 of the National Energy Code for Buildings. |  |  | Riviere-du-Loup | Quebec | 7A
18 | Thermopompe géothermique avec unité d'air d'appoint facultative | Ground-source heat pump with optional make-up air unit | [29 empty] | ToV5 | Régulation de la température d'alimentation | Supply temperature control | [32 empty] | Air conditioner, air-cooled, electric or no heating - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, ≥ 39.6 < 70.3 KW | 3.223 |  | 32 | Two speed, .5, fixed | 0.8 | 0.8 | 0.85 | 0.54897 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.8 | 0.6 | 0.5 | 0.5 | 0.51827 | 0.5 | 0.5 | 0.5 | 0.5 | 0.6 | 0.6 | 0.6 | 0.85 | 0.50613 | 0.5 | 0.54897 | 0.84897 | 0.50613 |  | 2 | 16 | 48 | 0.21962 | 0.00026351 | -1.3151e-08 | -0.085396 | -8.5567e-05 | 4.0562e-09 | HDD | [6 empty] | COP | COP | [13 empty] | Efficacité de la régulation du débit d'air | [5 empty] | Airflow control efficiency | Choisir dans la liste déroulant le type de contrôle pour le débit d'air d'alimentation utilisé pour ce système de CVCA. | Choose from the drop down list the type of supply airflow control applicable to this HVAC system. | [13 empty] | Code national de l'énergie pour les bâtiments | National Energy Code for Buildings | Code national de l'énergie pour les bâtiments | National Energy Code for Buildings |  |  | Thunder Bay | Ontario | 7A
19 | Éjecto-convecteur à deux tuyaux | Induction unit, two-pipe | [29 empty] | ToV6 | Efficacité de la régulation du débit d'air | Airflow control efficiency | [32 empty] | Air conditioner, air-cooled, electric or no heating - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, ≥ 70.3 < 223 kW | 2.93 |  | 32 | Constant | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5 |  | 2 | 17 | 49 | 0.004191 | -1.8139e-06 | 1.4837e-10 | -0.0075362 | 3.569e-06 | -2.9799e-10 | TDD | [6 empty] | W/W | W/W | [13 empty] | Pression statique totale du ventilateur d'alimentation | [5 empty] | Supply fan total static pressure | Entrer la pression statique totale de conception du ventilateur d'alimentation. Il ne faut pas confondre cette valeur avec la pression statique externe parfois indiquée dans les devis des appareils. | Enter the supply fan design total static pressure. It is important not to enter the external static pressure value, sometimes indicated on the equipment specifications. | [13 empty] | Auteur de la documentation | Documentation Author | Auteur de la documentation | Documentation Author |  |  | Red Deer | Alberta | 7A
20 | Éjecto-convecteur à quatre tuyaux | Induction unit, four-pipe | [29 empty] | ToV7 | Pression statique totale du ventilateur d'alimentation | Supply fan total static pressure | [32 empty] | Air conditioner, air-cooled, electric or no heating - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, >= 223 kW | 2.8421 | [31 empty] | 2 | 18 | 50 | -0.0065775 | 1.8738e-05 | -2.4567e-08 | 0.010451 | -1.2994e-05 | 1.5841e-08 | CDD | [6 empty] | Sélection | Selection | [13 empty] | Isolation des conduits de distribution | [5 empty] | Supply duct insulation | Entrer la valeur moyenne de l'isolation des gaines d'alimentation du système de CVCA. | Enter the average insulation value for the supply ducts served by this HVAC system. | [13 empty] | Le professionnel chargé de la coordination atteste par les présentes que la conception proposée représentée dans les documents de construction et modélisée pour cette demande de permis concorde avec tous les autres formulaires et feuilles de travail, spécifications et autres calculs soumis avec cette demande de permis. Le bâtiment proposé, dans sa conception actuelle, répond aux exigences du Code national de l’énergie pour les bâtiments. | The Coordinating Professional hereby certifies that the proposed building design represented in the construction documents and modelled for this permit application are consistent with all other forms and worksheets, specifications, and other calculations submitted with this permit application. The proposed building, as designed, meets the requirements of the National Energy Code for Buildings. | Le professionnel chargé de la coordination atteste par les présentes que la conception proposée représentée dans les documents de construction et modélisée pour cette demande de permis concorde avec tous les autres formulaires et feuilles de travail, spécifications et autres calculs soumis avec cette demande de permis. Le bâtiment proposé, dans sa conception actuelle, répond aux exigences du Code national de l’énergie pour les bâtiments. | The Coordinating Professional hereby certifies that the proposed building design represented in the construction documents and modelled for this permit application are consistent with all other forms and worksheets, specifications, and other calculations submitted with this permit application. The proposed building, as designed, meets the requirements of the National Energy Code for Buildings. |  |  | Regina | Saskatchewan | 7A
21 | Éjecto-convecteur à trois tuyaux | Induction unit, three-pipe | [29 empty] | ToV8 | Isolation des conduits de distribution | Supply duct insulation | [32 empty] | Air conditioner, water & evaporatively cooled, electric or no heating - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB, ≥ 19.0 < 39.6 kW | 3.3695 | [31 empty] | 2 | 19 | 51 | 0.0022576 | -3.0625e-07 | 3.0704e-11 | -0.00032511 | 9.9544e-08 | -8.482e-12 | HDD | [6 empty] | Sélection | Selection | [13 empty] | Pression statique totale du ventilateur de reprise | [5 empty] | Return fan total static pressure | Entrer la pression statique totale de conception du ventilateur de retour. Il ne faut pas confondre cette valeur avec la pression statique externe parfois indiquée dans les devis des appareils. | Enter the return fan design total static pressure. It is important not to enter the external static pressure value, sometimes indicated on the equipment specifications. | [13 empty] | J’affirme par les présentes que je suis éligible, en vertu des dispositions des autorités compétentes, à signer ce document à titre de responsable de sa préparation et que je détiens le titre d’ingénieur civil, d’ingénieur en mécanique, d’ingénieur en électrique ou d’architecte. | I hereby affirm that I am eligible, under the provisions of the authorities having jurisdiction, to sign this document as the person responsible for its preparation; and that I am licensed as a civil engineer, mechanical engineer, electrical engineer or architect. | J’affirme par les présentes que je suis éligible, en vertu des dispositions des autorités compétentes, à signer ce document à titre de responsable de sa préparation et que je détiens le titre d’ingénieur civil, d’ingénieur en mécanique, d’ingénieur en électrique ou d’architecte. | I hereby affirm that I am eligible, under the provisions of the authorities having jurisdiction, to sign this document as the person responsible for its preparation; and that I am licensed as a civil engineer, mechanical engineer, electrical engineer or architect. |  |  | Bagotville | Quebec | 7A
22 | CA intégré local, bibloc | Packaged terminal AC - split | [29 empty] | ToV9 | Pression statique totale du ventilateur de reprise | Return fan total static pressure | [32 empty] | Air conditioner, water & evaporatively cooled, electric or no heating - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB, ≥ 39.6 < 70.3 kW | 3.223 | [31 empty] | 2 | 20 | 52 | -0.00010686 | 2.8905e-06 | -3.909e-09 | 8.0458e-06 | -1.6932e-07 | 2.2119e-10 | CDD | [6 empty] | % | % | [13 empty] | Chute de température de calcul des serpentins de chauffage | [5 empty] | Heating coil design temperature drop | Entrer la valeur de conception pour le différentiel de température des serpentins de chauffage du système de CVCA. Utiliser la valeur moyenne pondérée selon la puissance dans le cas où plusieurs serpentins sont présents. | Enter the design temperature differential for the HVAC system heating coil. If multiple coils are present, use the capacity-weighted average value. | [13 empty] | J’affirme que j’ai le droit de signer ce document à titre de responsable de sa préparation; et pour la raison suivante | I affirm that I am eligible to sign this document as the person responsible for its preparation; and for the following reason: | J’affirme que j’ai le droit de signer ce document à titre de responsable de sa préparation; et pour la raison suivante | I affirm that I am eligible to sign this document as the person responsible for its preparation; and for the following reason: |  |  | Kenora | Ontario | 7A
23 | Rayonnement (plancher, plafond) avec unité d'air d'appoint facultative | Radiant (in-floor, ceiling) with optional make-up air unit | [29 empty] | ToV10 | Chute de température de calcul des serpentins de chauffage | Heating coil design temperature drop | [32 empty] | Air conditioner, water & evaporatively cooled, electric or no heating - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB, ≥ 70.3 kW | 3.223 | [31 empty] | 2 | 21 | 53 | -1.7736e-05 | -1.6224e-08 | 8.948e-13 | -7.7468e-08 | 3.9343e-11 | -2.7933e-15 | HDD | [6 empty] | % | % | [13 empty] | Chute de température de calcul des plinthes de chauffage | [5 empty] | Baseboard heater design temperature drop | Entrer la valeur de conception pour le différentiel de température des plinthes de chauffage. | Enter the design temperature differential for the baseboard heaters. | [13 empty] | Professionnel chargé de la coordination : | Coordinating Professional: | Professionnel chargé de la coordination : | Coordinating Professional: |  |  | Winnipeg | Manitoba | 7A
24 | Poutres refroidies avec unité d'air d'appoint facultative | Active chilled beams with optional make-up air unit | [29 empty] | ToV11 | Chute de température de calcul des plinthes de chauffage | Baseboard heater design temperature drop | [32 empty] | Heat pump, electric or no heating - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB, ≥ 19.0 < 39.6 kW | 3.223 | [31 empty] | 2 | 22 | 54 | -1.6917e-05 | -1.8169e-07 | 1.9991e-10 | 2.462e-07 | -1.141e-09 | 1.1958e-12 | CDD | [6 empty] | Valeur RSI | RSI Value | [13 empty] | Efficacité de chauffage des chaudières/générateurs d'air chaud/thermopompes | [5 empty] | Boiler/furnace/heat pump heating efficiency | Entrer l'efficacité de l'appareil de chauffage du système. Dans le cas des pompes à chaleur, le rendement doit être exprimé en termes de fraction, comme par exemple 0.83 pour représenter 83%. Pour les petits systèmes où uniquement le AFUE est disponible, utiliser directement cette valeur. Si plus d'un appareil dessert le système, il faut spécifier l'efficacité moyenne pondérée selon la puissance des appareils. Dans le cas ou plus d'une source d'énergie est présente, il faut sélectionner l'équipement qui fournit la majorité de l'énergie de chauffage. | Enter the heating equipment efficiency. For heat pumps, the COP must be expressed as fractions, such as 0.83 for 83% efficiency. For smaller equipment where only the AFUE is available, enter this value directly. If more than one piece of equipment is serving the system, enter the capacity-weighted average efficiency. If multiple energy sources are used, the fuel source of equipment providing the majority of the heating load must be selected. | [13 empty] | Date : | Date: | Date : | Date: |  |  | Saskatoon | Saskatchewan | 7A
25 | Générateur de chaleur suspendu | Unit heater | [29 empty] | ToV12 | Efficacité de chauffage des chaudières/générateurs d'air chaud/thermopompes | Boiler/furnace/heat pump heating efficiency | [32 empty] | Heat pump, electric or no heating - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB, ≥ 39.6 < 70.3 kW | 3.1058 |  |  | French | English | [27 empty] | 2 | 23 | 55 | 0.0067478 | 3.9025e-06 | -2.1933e-10 | -0.0031305 | -2.6279e-06 | 1.7444e-10 | HDD | [6 empty] | Valeur RSI | RSI Value | [13 empty] | Efficacité de refroidissement des refroidisseurs/systèmes à détente directe/thermopompes | [5 empty] | Chillers/direct expansion system/heat pump cooling efficiency | Entrer l'efficacité de conception de l'équipement de refroidissement. L'efficacité doit toujours être définie en terme de COP. Si plus d'un appareil dessert le système, on doit définir l'efficacité moyenne pondérée selon la puissance des appareils. | Enter the cooling equipment efficiency. All efficiencies have to be entered in terms of COP. If more than one piece of equipment is serving the system, enter the capacity-weighted average efficiency. | [13 empty] | Signature : | Signature: | Signature : | Signature: |  |  | Grande Prairie | Alberta | 7B
26 | Ventilo-convecteur | Unit ventilator | [29 empty] | ToV13 | Efficacité de refroidissement des refroidisseurs/systèmes à détente directe/thermopompes | Chillers/direct expansion system/heat pump cooling efficiency | [32 empty] | Heat pump, electric or no heating - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB, ≥ 70.3 kW | 2.7835 |  |  | Rajustement AE d'alimentation | Supply OA Reset | [27 empty] | 2 | 24 | 56 | -0.0045633 | 7.5437e-05 | -8.3006e-08 | 0.0035424 | -4.6858e-05 | 5.2179e-08 | CDD | [6 empty] | kPa | kPa | [13 empty] | Rapport de puissance d'entrée du ventilateur de rejet | [5 empty] | Rejection fan input power ratio | Définir la puissance unitaire des ventilateurs du système de rejet de chaleur. Cette valeur représente la puissance totale installée des ventilateurs sur la puissance de conception des équipements de rejet de chaleur. | Enter the heat rejection equipment unitary fan power. This value represents the ratio of the total installed fan power of the equipment divided by its heat rejection capacity, expressed in the same unit. | [13 empty] | Cochez une | Check One | Cochez une | Check One |  |  | Fort St. John | Br. Columbia | 7B
27 | Rayonnement avec unité d'air d'appoint facultative | Radiation with optional make-up air unit | [29 empty] | ToV14 | Rapport de puissance d'entrée du ventilateur de rejet | Rejection fan input power ratio | [32 empty] | Air conditioner, air-cooled, all other heating section - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, >=19 <40 | 3.223 |  |  | Température la plus chaude | Warmest | [27 empty] | 2 | 25 | 57 | 0.0031782 | 3.5663e-06 | -2.3018e-10 | -0.00079537 | -1.5049e-06 | 1.0279e-10 | HDD | [6 empty] | kPa | kPa | [13 empty] | Refroidissement par utilisation directe de l'air extérieur (économiseur sur le circuit d'air) | [5 empty] | Cooling by direct use of outdoor air (air economizer) | Sélectionner le type de refroidissement par utilisation de l'air extérieur (TTS = température du thermomètre sec). | Select the type of air-side economizer used in this HVAC system. | [13 empty] | Résultats sommaires de conformité | Summary compliance results | Résultats sommaires de conformité | Summary compliance results |  |  | Brandon | Manitoba | 7B
[32 empty] | ToV15 | Refroidissement par utilisation directe de l'air extérieur (économiseur sur le circuit d'air) | Cooling by direct use of outdoor air (air economizer) | [32 empty] | Air conditioner, air-cooled, all other heating section - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB | 3.1644 |  |  | Constant > 15°C | Constant > 15°C | [27 empty] | 2 | 26 | 58 | 0.0013324 | 1.5488e-05 | -7.9306e-09 | -0.00089978 | -1.8283e-06 | -3.2757e-09 | CDD | [6 empty] | % | % | [13 empty] | Régulation du débit d'air extérieur | [5 empty] | Outdoor airflow control | Sélectionner le type de contrôle de l'air extérieur admis dans le système de CVCA (CVD = contrôle de ventilation selon la demande). | Select the type of outdoor air control used for this HVAC system (DCV = Demand control ventilation). | [13 empty] | Code national de l'énergie pour les bâtiments – 2011 | National Energy Code of Canada for Buildings – 2011 | Code national de l'énergie pour les bâtiments – 2011 | National Energy Code of Canada for Buildings – 2011 |  |  | Dauphin | Manitoba | 7B
[32 empty] | ToV16 | Régulation du débit d'air extérieur | Outdoor airflow control | [32 empty] | Air conditioner, air-cooled, all other heating section - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB | 2.8714 |  |  | Constant <= 15°C | Constant <= 15°C | [27 empty] | 2 | 27 | 59 | 1558.2371 | -0.57527 | 4.7368e-05 | -984.5869 | 0.36377 | -2.9957e-05 | HDD | [6 empty] | % | % | [13 empty] | Efficacité de récupération de chaleur dans l'air d'évacuation | [5 empty] | Exhaust air heat-recovery efficiency | Entrer l'efficacité de conception du système de récupération de chaleur sur l'air évacué. | Enter the design heat recovery effectiveness. | [19 empty] | Timmins | Ontario | 7B
| DWH | [30 empty] | ToV17 | Efficacité de récupération de chaleur dans l'air d'évacuation | Exhaust air heat-recovery efficiency | [32 empty] | Air conditioner, air-cooled, all other heating section - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, >= 223 kW | 2.7835 |  |  | VAIAL | Forward curve with vanes | [27 empty] | 2 | 28 | 60 | 341.2591 | -1.9805 | 0.0026043 | -208.9971 | 1.216 | -0.0015979 | CDD | [6 empty] | % | % | [13 empty] | Refroidissement par utilisation indirecte de l'air extérieur (économiseur sur le circuit d'eau) | [5 empty] | Cooling by indirect use of outdoor air (water economizer) | Entrer l'efficacité de conception de l'échangeur servant au refroidissement sur le circuit d'eau. | Enter the design water-side cooling coil heat exchange effectiveness. | [19 empty] | Sept-Iles | Quebec | 7B
| Tank | 1 | [29 empty] | ToV18 | Refroidissement par utilisation indirecte de l'air extérieur (économiseur sur le circuit d'eau) | Cooling by indirect use of outdoor air (water economizer) | [32 empty] | Air conditioner, water & evaporatively cooled, all other heating section - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | 3.3109 |  |  | Moteur à vitesse variable | VSD | [27 empty] | 2 | 29 | 61 | -190.8361 | 0.071769 | -5.9915e-06 | 118.8875 | -0.044448 | 3.708e-06 | HDD | [6 empty] | % | % | [13 empty] | Isolation de la tuyauterie - Eau chaude | [5 empty] | Piping insulation - hot water | Entrer la valeur moyenne de l'isolation de la tuyauterie d'eau chaude. | Enter the average piping insulation value. | [19 empty] | Val d'Or | Quebec | 7B
| Tankless (instantaneous) | 2 | [29 empty] | ToV19 | Isolation de la tuyauterie - Eau chaude | Piping insulation - hot water | [32 empty] | Air conditioner, water & evaporatively cooled, all other heating section - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | 3.1644 |  |  | VAPAL | Airfoil with inlet vanes | [27 empty] | 2 | 30 | 62 | -43.4659 | 0.20821 | -0.00019981 | 27.3265 | -0.1273 | 0.00012122 | CDD | [6 empty] | Sélection | Selection | [13 empty] | Isolation de la tuyauterie - Eau réfrigérée | [5 empty] | Piping insulation - chilled water | Entrer la valeur moyenne de l'isolation de la tuyauterie d'eau réfrigérée. | Enter the average piping insulation value. | [19 empty] | Battle Harbour (St Anthony) | Newfoundland | 7B
| Space-heating boiler | 3 | [29 empty] | ToV20 | Isolation de la tuyauterie - Eau réfrigérée | Piping insulation - chilled water | [32 empty] | Air conditioner, water & evaporatively cooled, all other heating section - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | 3.1644 |  |  | VAPA | Riding fan curve | [27 empty] | 2 | 31 | 63 | -65.0211 | 0.026638 | -2.3981e-06 | 40.7201 | -0.016484 | 1.4885e-06 | HDD | [6 empty] | Sélection | Selection | [13 empty] | Pertes de pression dans la tuyauterie - Eau chaude | [5 empty] | Piping pressure losses - hot water | Entrer la perte de charge totale du système de chauffage à eau chaude. Dans le cas de système multiple, spécifier la pression de tête équivalente calculée selon le débit et la perte de pression de l'ensemble des circuits rapporté selon le débit de la boucle la plus importante. | Enter the total hydronic heating system pressure losses. In the case of multiple loops associated with a single HVAC system, enter the equivalent head calculated using the flow and head of each loop and expressed as an equivalent head for the loop having the largest flow rate. | [19 empty] | Peace River | Alberta | 7B
[32 empty] | ToV21 | Pertes de pression dans la tuyauterie - Eau chaude | Piping pressure losses - hot water | [32 empty] | Heat pump, all other heating section - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | 3.1644 |  |  | TTS Double | Dual DBT | [27 empty] | 2 | 32 | 64 | -81.2787 | 0.23 | 3.7482e-06 | 50.808 | -0.14077 | -5.348e-06 | CDD | [6 empty] | Sélection | Selection | [13 empty] | Pertes de pression dans la tuyauterie - Eau réfrigérée | [5 empty] | Piping pressure losses - chilled water | Entrer la perte de charge totale du système d'eau refroidie. Dans le cas de système multiple, spécifier la pression de tête équivalente calculée selon le débit et la perte de pression de l'ensemble des circuits rapporté selon le débit de la boucle la plus importante. | Enter the total hydronic cooling system pressure losses. In the case of multiple loops associated with a single HVAC system, enter the equivalent head calculated using the flow and head of each loop and expressed as an equivalent head for the loop having the largest flow rate. | [19 empty] | Kapuskasing | Ontario | 7B
[32 empty] | ToV22 | Pertes de pression dans la tuyauterie - Eau réfrigérée | Piping pressure losses - chilled water | [32 empty] | Heat pump, all other heating section - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | 3.0472 |  |  | Enthalpie | Enthalpy | [27 empty] | 3 | 1 | 65 | 5.393 | -0.0013425 | 8.8288e-08 | -3.7572 | 0.00091206 | -5.9166e-08 | HDD | [6 empty] | Sélection | Selection | [13 empty] | Efficacité mécanique des pompes - Eau chaude | [5 empty] | Pump mechanical efficiency - hot water | Entrer le rendement mécanique de conception des pompes. Dans le cas où le système est doté de plusieurs pompes, définir la valeur moyenne pondérée selon la puissance des pompes. | Enter the pump motor efficiency. When multiple pumps serve the system, use the power-weighted average pump efficiency. | [19 empty] | Prince Albert | Saskatchewan | 7B
[32 empty] | ToV23 | Efficacité mécanique des pompes - Eau chaude | Pump mechanical efficiency - hot water | [32 empty] | Heat pump, all other heating section - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | 2.7249 |  |  | Enthalpie double | Dual Enthalpy | [27 empty] | 3 | 2 | 66 | 2.5295 | -0.00062153 | 4.0567e-08 | -0.8585 | 0.0002017 | -1.2835e-08 | HDD | [6 empty] | Sélection | Selection | [13 empty] | Efficacité mécanique des pompes - Eau réfrigérée | [5 empty] | Pump mechanical efficiency - chilled water | Entrer le rendement mécanique de conception des pompes. Dans le cas où le système est doté de plusieurs pompes, définir la valeur moyenne pondérée selon la puissance des pompes. | Enter the pump motor efficiency. When multiple pumps serve the system, use the power-weighted average pump efficiency. | [19 empty] | Fort McMurray | Alberta | 7B
| The sum of the faucet flow ratio and the shower flow ratio must not exceed 100%. | [30 empty] | ToV24 | Efficacité mécanique des pompes - Eau réfrigérée | Pump mechanical efficiency - chilled water | [32 empty] | Large condensing units - RCU-A | 2.9593 |  |  | Fixe | Fixed | [27 empty] | 3 | 3 | 67 | 5.3904 | -0.0013215 | 8.6941e-08 | -5.3957 | 0.0012992 | -8.4683e-08 | HDD | [6 empty] | Sélection | Selection | [13 empty] | Efficacité des moteurs de pompe - Eau chaude | [5 empty] | Pump motor efficiency - hot water | Entrer le rendement de conception des moteurs des pompes. Dans le cas où le système est doté de plusieurs pompes, définir la valeur moyenne pondérée selon la puissance des moteurs. | Enter the design efficiency of the pump motor. When multiple pumps serve the system, use the power-weighted average motor efficiency. | [19 empty] | Cartwright (Happy Valley - Goose Bay) | Newfoundland | 7B
|  | The sum of the faucet flow ratio and the shower flow ratio must not exceed 100%. | [29 empty] | ToV25 | Efficacité des moteurs de pompe - Eau chaude | Pump motor efficiency - hot water | [32 empty] | Large condensing units - RCU-E, RCU-W | 3.8383 | COP |  | Thermomètre sec | Dry Bulb | [27 empty] | 3 | 4 | 68 | 2.1422 | -0.00052671 | 3.4707e-08 | -0.88902 | 0.00021458 | -1.4007e-08 | HDD | [6 empty] | W | W | [13 empty] | Efficacité des moteurs de pompe - Eau réfrigérée | [5 empty] | Pump motor efficiency - chilled water | Entrer le rendement de conception des moteurs des pompes. Dans le cas où le système est doté de plusieurs pompes, définir la valeur moyenne pondérée selon la puissance des moteurs. | Enter the design efficiency of the pump motor. When multiple pumps serve the system, use the power-weighted average motor efficiency. | [19 empty] | Happy Valley - Goose Bay | Newfoundland | 7B
| HVAC Type ID - | La somme du coefficient de débit des robinets et du coefficient de débit des douches ne doit pas dépasser 100%. | [29 empty] | ToV26 | Efficacité des moteurs de pompe - Eau réfrigérée | Pump motor efficiency - chilled water | [32 empty] | Condensing unit - Air-cooled >= 73 (250000) | 2.96 | COP |  | Fraction horaire | Fraction of hourly | [27 empty] | 3 | 5 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [21 empty] | Régulation de la pompe d'eau chaude | [5 empty] | Hot water pump control | Sélectionner le type de régulation applicable aux pompes d'eau chaude. | Select the hot water pump control logic applicable to this system. | [19 empty] | The Pas | Manitoba | 7B
| HVAC Type ID - | [30 empty] | ToV27 | Régulation de la pompe d'eau chaude | Hot water pump control | [32 empty] | Condensing unit - Water evaporatively cooled >= 73 (250000) | 3.84 | COP |  | CVD reprise | DCV Return | [27 empty] | 3 | 6 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | TDD | [21 empty] | Régulation de la pompe d'eau réfrigérée | [5 empty] | Chilled water pump control | Sélectionner le type de régulation applicable aux pompes d'eau réfrigérée. | Select the chilled water pump control logic applicable to this system. | [19 empty] | Whitehorse | Yukon | 7B
| Type d'installation CVCA | [30 empty] | ToV28 | Régulation de la pompe d'eau réfrigérée | Chilled water pump control | [32 empty] | Ground or water source heat pumps < 35 (119500) - open systems | 4.75 |  |  | CVD alimentation | DCV Supply | [27 empty] | 3 | 7 | 71 | -0.92455 | 0.0002561 | -1.7769e-08 | 0.10998 | -3.3867e-05 | 2.4607e-09 | HDD | [21 empty] | Régulation de la température boucle d'eau chaude | [5 empty] | Hot water loop temperature control | Sélectionner le type de régulation de température applicable au réseau d'eau chaude. | Select the hot water temperature control logic applicable to this system. | [19 empty] | Whitehorse | Yukon | 7B
[32 empty] | ToV29 | Régulation de la température boucle d'eau chaude | Hot water loop temperature control | [32 empty] | Ground or water source heat pumps < 35 (119500) - closed systems | 3.93 |  |  | CVD frac. Horaire, reprise | DCV, fraction of hourly, Return | [27 empty] | 3 | 8 | 72 | 0.009111 | 2.8165e-06 | -2.7098e-10 | -0.00093432 | -2.9138e-07 | 2.8015e-11 | HDD | [21 empty] | Régulation de la température boucle d'eau réfrigérée | [5 empty] | Chilled water loop temperature control | Sélectionner le type de régulation de température applicable au réseau d'eau réfrigérée. | Select the chilled water temperature control logic applicable to this system. | [19 empty] | Fort Nelson | Br. Columbia | 8
| SWH Type ID - | [30 empty] | ToV30 | Régulation de la température boucle d'eau réfrigérée | Chilled water loop temperature control | [32 empty] | Internal water-loop heat pumps < 40 (136500) | 3.52 |  |  | Fixe | Fixed | [27 empty] | 3 | 9 | 73 | 0.66049 | -0.00015697 | 9.9313e-09 | -1.0823 | 0.00027383 | -1.8302e-08 | TDD | [21 empty] | Régulation du débite d'eau chaude | [5 empty] | Hot water flow control | Sélectionner le type de régulation de débit aux pompes d'eau chaude. Dans le cas ou plusieurs pompes ont une régulation différente, sélectionner celle qui est applicable à la majorité de la force motrice. (VV = vitesse variable) | Select the hot water pump flow control applicable to this system. In the case where multiple pumps used different controls, select the type that controls the majority of the pump installed power. | [19 empty] | Big Trout Lake | Ontario | 8
| SWH Type ID - | [30 empty] | ToV31 | Régulation du débit d'eau chaude | Hot water flow control | [32 empty] | Water-cooled air conditioners < 19 (65000) | 3.54 | COP |  | Demande seulement | Demand-only | [27 empty] | 3 | 10 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [21 empty] | Régulation du débite d'eau réfrigérée | [5 empty] | Chilled water flow control | Sélectionner le type de régulation de débit aux pompes d'eau réfrigérée. Dans le cas ou plusieurs pompes ont une régulation différente, sélectionner celle qui est applicable à la majorité de la force motrice. (VV = vitesse variable) | Select the chilled water pump flow control applicable to this system. In the case where multiple pumps used different controls, select the type that controls the majority of the pump installed power. | [19 empty] | Fort Smith | Northwest Terr. | 8
| Type d'installation SWH | [30 empty] | ToV32 | Régulation du débit d'eau réfrigérée | Chilled water flow control | [32 empty] | Water-cooled air conditioners >= 19 kW and < 40 kW electric resistance heating (or none) | 3.37 | COP |  | Veille | Standby | [27 empty] | 3 | 11 | 75 | -0.00010097 | -1.5463e-08 | 1.3227e-12 | 3.3468e-06 | 5.214e-10 | -4.5183e-14 | HDD | [27 empty] | System Type | Choisir un système parmi les 27 installations CVCA offerts dans la liste déroulante et tel que présenté dans la tableau 5.3.1.1 du CNÉB. Les composantes applicables au système deviennent alors visibles. Si certaines composantes ne sont toutefois pas applicables au système spécifique du bâtiment, les valeurs de référence doivent obligatoirement être conservées par l'utilisateur dans le cadre de l'évaluation de conformité. | Choose from the list of 27 HVAC System Types ID available in the drop down list and as provided in Table 5.3.1.1 of the NECB. The components that are applicable to the system will then be visible. In all instances where a visible component is NOT part of the system being evaluated, its value must be defined as identical to that of the Reference value for a compliance calculation. | [19 empty] | Thompson | Manitoba | 8
[67 empty] | Water-cooled air conditioners >= 19 kW and < 40 kW all other | 3.31 | COP |  | Zone de délestage | Snap zone | [27 empty] | 3 | 12 | 76 | 0.55147 | 5.0696e-05 | 1.3274e-09 | 0 | 0 | 0 | HDD | [27 empty] | Cooling System Type | Choisir le type de système de refroidissement associé au système de CVCA, tel que défini dans le tableau 5.2.12.1 of the CNÉB. | Choose the type of cooling equipment associated with this HVAC system as defined in Table 5.2.12.1 of the NECB. | [19 empty] | Uranium City | Saskatchewan | 8
[67 empty] | Water-cooled air conditioners >= 40 kW and < 70 kW electric resistance heating (or none) | 3.22 | COP |  | Programmé | Scheduled | [27 empty] | 3 | 13 | 77 | 0.17109 | 0.00062021 | -6.9737e-07 | -0.019753 | -4.9293e-05 | 5.3927e-08 | CDD | [27 empty] | Cooling Sub-System Type | Choisir le type particulier d'appareil associé au système de refroidissement, tel que défini dans le tableau 5.2.12.1 of the CNÉB. | Choose the precise category associated with the cooling equipment system type, as defined in Table 5.2.12.1 of the NECB. | [19 empty] | Wabush | Newfoundland | 8
[67 empty] | Water-cooled air conditioners >= 40 kW and < 70 kW all other | 3.16 | COP |  | Délestage à l'extérieur | Snap outdoor | [27 empty] | 3 | 14 | 78 | -0.63456 | -0.0059907 | 5.907e-06 | 42.1264 | -0.41537 | 0.00056557 | CDD | [27 empty] | Cooling capacity | Cette valeur ne sert uniquement qu'à définir le rendement de référence de certains appareils de refroidissement, tel que défini dans le tableau 5.2.12.1 du CNÉB. | This value only serves in defining the Reference value performance for certain type of cooling equipment, as defined in Table 5.2.12.1 of the NECB. | [19 empty] | Nitchequon | Quebec | 8
| Incomplete Data | Incomplete Data | [64 empty] | Water-cooled air conditioners >= 70 kW electric resistance heating (or none) | 3.22 | COP |  | Demande seulement | Demand-only | [27 empty] | 3 | 15 | 79 | -0.087536 | 0.0026927 | -4.2165e-06 | 0.049955 | -0.0015367 | 2.4063e-06 | CDD | [27 empty] | Heating System Type | Choisir le type de système de chauffage associé au système de CVCA, tel que défini dans le tableau 5.2.12.1 of the CNÉB. Pour les cas de chauffage à résistance électrique, choisir une chaudière électrique. Toutefois, dans ce cas, les valeurs de référence pour le système de distribution à eau chaude doivent alors être conservées. | Choose the type of heating equipment associated with this HVAC system as defined in Table 5.2.12.1 of the NECB. For all resistance electric heating cases, the user must select "Electric boilers". However, in this case, all of the components relating to the hot water distribution system must be defined using the Reference values. | [19 empty] | Kuujjuarapik | Quebec | 8
|  | Données Incomplètes | [64 empty] | Water-cooled air conditioners >= 70 kW all other | 3.16 | COP |  | Veille | Standby | [27 empty] | 3 | 16 | 80 | -0.15391 | 6.6274e-05 | -5.1861e-09 | -0.083969 | 4.5083e-05 | -2.1358e-09 | TDD | [49 empty] | Schefferville | Quebec | 8
[67 empty] | Direct-expansion ground-source heat pumps <= 21 (71700) | 3.809 |  |  | Zone de délestage | Snap zone | [27 empty] | 3 | 17 | 81 | 0.15705 | -1.2389e-05 | 1.2536e-09 | -0.64377 | 0.0002388 | -1.3248e-08 | TDD | [49 empty] | Yellowknife | Northwest Terr. | 8
[67 empty] | PTAC and PTHP air-cooled electrically operated - Electrically Operated | -1 |  |  | Programmé | Scheduled | [27 empty] | 3 | 18 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Kuujuaq | Quebec | 8
[67 empty] | PTHP in cooling mode (Standard rating) | -2 |  |  | Délestage à l'extérieur | Snap outdoor | [27 empty] | 3 | 19 | 83 | 0.1643 | -3.981e-05 | 2.6442e-09 | -0.010578 | 2.581e-06 | -1.723e-10 | HDD | [49 empty] | Norman Wells | Northwest Terr. | 8
[67 empty] | PTHP in heating mode (Standard rating) | -3 |  |  | Fixe | Fixed | [27 empty] | 3 | 20 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Churchill | Manitoba | 8
[67 empty] | Room air conditioners with reserve cycle with louvered sides < 10.55 (36000) | 2.4905 |  |  | Programmé | Scheduled | [27 empty] | 3 | 21 | 85 | -0.00025807 | -2.9184e-08 | 2.7248e-12 | -1.6282e-07 | 1.4109e-10 | -1.3271e-14 | HDD | [49 empty] | Inuvik | Northwest Terr. | 8
[67 empty] | Room air conditioners with reserve cycle without louvered sides < 10.55 (36000) | 2.344 |  |  | Correction chaud-froid | Load reset | [27 empty] | 3 | 22 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Iqualuit | Nunavut | 8
[67 empty] | Room air conditioners without reverse cycle < 10.55 (36000) | 2.4905 |  |  | Rajustement AE, min 140 °F | OA Reset, min 140 °F | [27 empty] | 3 | 23 | 87 | 0.27768 | -5.9297e-05 | 3.9094e-09 | -0.15039 | 3.1834e-05 | -2.1099e-09 | HDD | [49 empty] | Inuvik (NWT) | Yukon | 8
[67 empty] | Room air conditioners with louvered sides < 1.8 kW | 2.84 |  |  | Rajustement AE, min >140 °F | OA Reset, min >140 °F | [27 empty] | 3 | 24 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Chesterfield Inlet | Nunavut | 8
[67 empty] | Room air conditioners with louvered sides >= 1.8 kW and < 2.3 kW | 2.84 |  |  | Fixe | Fixed | [27 empty] | 3 | 25 | 89 | 0.11099 | -1.1423e-05 | 3.7958e-10 | -0.051101 | 7.041e-06 | -3.2427e-10 | HDD | [49 empty] | Coral Harbour | Nunavut | 8
[67 empty] | Room air conditioners with louvered sides >= 2.3 kW and < 4.1 kW | 2.87 |  |  | Programmé | Scheduled | [27 empty] | 3 | 26 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Cambridge Bay | Nunavut | 8
[67 empty] | Room air conditioners with louvered sides >= 4.1 kW and < 5.9 kW | 2.84 |  |  | Correction chaud-froid | Load reset | [27 empty] | 3 | 27 | 91 | -105.4759 | 0.035577 | -2.6002e-06 | 66.7369 | -0.022135 | 1.6094e-06 | HDD
[67 empty] | Room air conditioners with louvered sides >= 5.9 kW | 2.49 |  |  | Rajustement AW, min 58 °F | OA Reset, min 58 °F | [27 empty] | 3 | 28 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Zones climatiques |  | Climate Zones
[67 empty] | Room air conditioners without louvered sides < 2.3 kW | 2.64 |  |  | Rajustement AE, min <54 °F | OA Reset, min <54 °F | [27 empty] | 3 | 29 | 93 | 41.1443 | -0.014233 | 1.0951e-06 | -19.5249 | 0.0071511 | -5.6153e-07 | HDD | [49 empty] | Ville / Emplacement | Province/Territoire | City / Location | Province/Territory
[67 empty] | Room air conditioners wothout louvered sides >= 2.3 kW and < 5.9 kW | 2.49 |  |  | VV, réenclenchement vanne | VSD, valve reset | [27 empty] | 3 | 30 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Vancouver | Colombie Brit. | Vancouver | Br. Columbia
[67 empty] | Room air conditioners without louvered sides >= 5.9 kW | 2.49 |  |  | Deux vitesses, .67 | Two speed, .67 | [27 empty] | 3 | 31 | 95 | 10.7728 | -0.002434 | 9.3305e-08 | -9.6003 | 0.0024076 | -9.4537e-08 | HDD | [49 empty] | Abbotsford | Colombie Brit. | Abbotsford | Br. Columbia
[67 empty] | Room air conditioner heat pumps with louvered sides < 5.9 kW | 2.65 |  |  | VV, fixe | VSD, fixed | [27 empty] | 3 | 32 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Tofino | Colombie Brit. | Tofino | Br. Columbia
[67 empty] | Room air conditioner heat pumps with louvered sides < 5.9 kW | 2.49 |  |  | Deux vitesses, .5 | Two speed, .5 | [27 empty] | 4 | 1 | 97 | 3.6211 | -0.00086842 | 5.6743e-08 | -2.0181 | 0.00047026 | -3.0307e-08 | HDD | [49 empty] | Penticton | Colombie Brit. | Penticton | Br. Columbia
[67 empty] | Room air conditioner heat pumps without louvered sides < 4.1 | 2.49 |  |  | Constant | Constant | [27 empty] | 4 | 2 | 98 | 2.2545 | -0.00053616 | 3.4803e-08 | -0.80914 | 0.00018496 | -1.1751e-08 | HDD | [49 empty] | Penticton | Colombie Brit. | Penticton | Br. Columbia
[67 empty] | Room air conditioner heat pumps without louvered sides >= 4.1 | 2.34 |  |  | VV, réenclenchement vanne | VSD, valve reset | [27 empty] | 4 | 3 | 99 | 4.0438 | -0.0009642 | 6.3693e-08 | -4.103 | 0.00096375 | -6.3288e-08 | HDD | [49 empty] | Port Hardy | Colombie Brit. | Port Hardy | Br. Columbia
[67 empty] | Room air conditioner casement only | 2.55 |  |  | Deux vitesses, .67, réencl., vanne | Two speed, .67, valve reset | [27 empty] | 4 | 4 | 100 | 1.6364 | -0.00039312 | 2.602e-08 | -0.69507 | 0.00016484 | -1.085e-08 | HDD | [49 empty] | Windsor | Ontario | Windsor | Ontario
[67 empty] | Room air conditioner casement slider | 2.78 |  |  | VV, fixe | VSD, fixed | [27 empty] | 4 | 5 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Kamloops | Colombie Brit. | Kamloops | Br. Columbia
[67 empty] | Air-cooled < 19 (65000) | 2.09 |  |  | Deux vitesses, .5, fixe | Two speed, .5, fixed | [27 empty] | 4 | 6 | 102 | 0 | 0 | 0 | 0 | 0 | 0 | TDD | [49 empty] | Toronto | Ontario | Toronto | Ontario
[67 empty] | Air-cooled < 19 (65000) and < 70 (240000) | 1.99 |  |  | Constant | Constant | [27 empty] | 4 | 7 | 103 | -0.51 | 0.00013826 | -9.5266e-09 | 0.040235 | -1.2256e-05 | 8.8143e-10 | HDD | [49 empty] | Castlegar | Colombie Brit. | Castlegar | Br. Columbia
[67 empty] | Air-cooled >= 70 (240000) | 1.79 | [31 empty] | 4 | 8 | 104 | 0.044856 | -9.5554e-06 | 5.5633e-10 | -0.004359 | 9.0139e-07 | -5.1207e-11 | HDD | [49 empty] | Victoria | Colombie Brit. | Victoria | Br. Columbia
[67 empty] | Water-cooled < 19 (65000) | 2.49 | [31 empty] | 4 | 9 | 105 | -0.87944 | 0.00022849 | -1.559e-08 | 0.16967 | -5.0537e-05 | 3.6055e-09 | HDD | [49 empty] | Prince Rupert | Colombie Brit. | Prince Rupert | Br. Columbia
[67 empty] | Water-cooled >= 19 (65000) and < 70 (240000) | 2.39 | [31 empty] | 4 | 10 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Halifax | Nouvelle Écosse | Halifax | Nova Scotia
[67 empty] | Water-cooled >= 70 (240000) | 2.29 | [31 empty] | 4 | 11 | 107 | -0.00010097 | -1.5463e-08 | 1.3227e-12 | 3.3468e-06 | 5.214e-10 | -4.5183e-14 | HDD | [49 empty] | Yarmouth | Nouvelle Écosse | Yarmouth | Nova Scotia
[67 empty] | Water-cooled with fluid economizer < 19 (65000) | 2.44 | [31 empty] | 4 | 12 | 108 | 0.34967 | 7.6452e-05 | 3.2863e-10 | 0 | 0 | 0 | HDD | [49 empty] | London | Ontario | London | Ontario
[67 empty] | Water-cooled with fluid economizer >= 19 (65000) and < 70 (240000) | 2.34 | [31 empty] | 4 | 13 | 109 | -0.017459 | 0.00049779 | -5.9857e-07 | 0.0011624 | -3.0978e-05 | 3.7613e-08 | CDD | [49 empty] | Trenton | Ontario | Trenton | Ontario
[67 empty] | Water-cooled with fluid economizer >= 70 (240000) | 2.24 | [31 empty] | 4 | 14 | 110 | 0.0045329 | -0.00091105 | 6.5241e-07 | 0.21263 | -0.0014658 | 2.2614e-06 | CDD | [49 empty] | Montréal (Dorval) | Québec | Montreal (Dorval) | Quebec
[67 empty] | Glycol-cooled < 19 (65000) | 2.39 | [31 empty] | 4 | 15 | 111 | -0.0021572 | 0.0011113 | -1.8498e-06 | 0.0012311 | -0.0006342 | 1.0556e-06 | CDD | [49 empty] | Greenwood | Nouvelle Écosse | Greenwood | Nova Scotia
[67 empty] | Glycol-cooled >= 19 (65000) and 70 (240000) | 2.04 | [31 empty] | 4 | 16 | 112 | -0.20809 | 7.9699e-05 | -6.0273e-09 | 0.010008 | 4.9033e-06 | 1.1635e-09 | TDD | [49 empty] | Terrace | Colombie Brit. | Terrace | Br. Columbia
[67 empty] | Glycol-cooled >= 70 (240000) | 1.99 | [31 empty] | 4 | 17 | 113 | 0.585 | -0.00021016 | 1.8614e-08 | -1.0113 | 0.00041876 | -2.897e-08 | HDD | [49 empty] | Ottawa | Ontario | Ottawa | Ontario
[67 empty] | Glycol-cooled with fluid economizer < 19 (65000) | 2.34 | [31 empty] | 4 | 18 | 114 | -0.0041409 | 0.00020101 | -3.1204e-07 | 0.0029511 | -0.00013313 | 2.0708e-07 | CDD | [49 empty] | Charlottetown | Île-du-Prince-Édouard | Charlottetown | P.E.I.
[67 empty] | Glycol-cooled with fluid economizer >= 19 (65000) and < 70 (240000) | 1.99 | [31 empty] | 4 | 19 | 115 | 0.1643 | -3.981e-05 | 2.6442e-09 | -0.010578 | 2.581e-06 | -1.723e-10 | HDD | [49 empty] | St-Hubert | Québec | St. Hubert | Quebec
[67 empty] | Glycol-cooled with fluid economizer >= 70 (240000) | 1.94 | [31 empty] | 4 | 20 | 116 | -0.0020005 | 4.0484e-05 | -5.6551e-08 | 0.00017344 | -2.6171e-06 | 3.4236e-09 | CDD | [49 empty] | Lethbridge | Alberta | Lethbridge | Alberta
[67 empty] | Chilled water air handler < 19 (65000) | 6.06 | [31 empty] | 4 | 21 | 117 | -0.00022587 | -1.2473e-08 | 1.9239e-12 | -1.2704e-07 | 1.7503e-09 | -2.8409e-12 | HDD | [49 empty] | Cranbrook | Colombie Brit. | Cranbrook | Br. Columbia
[67 empty] | Chilled water air handler >= 19 (65000) and < 70 (240000) | 7.06 | [31 empty] | 4 | 22 | 118 | 0.00039255 | -1.2371e-05 | 1.6558e-08 | 1.2547e-07 | 2.2153e-08 | -2.7568e-11 | CDD | [49 empty] | Frédéricton | Nouveau-Brunswick | Fredericton | New Brunswick
[67 empty] | Chilled water air handler >= 70 (240000) | 9.06 | [31 empty] | 4 | 23 | 119 | 0.069153 | 2.439e-06 | -4.3826e-10 | -0.007812 | -0.00022482 | 3.3574e-07 | HDD | [49 empty] | Truro | Nouvelle Écosse | Truro | Nova Scotia
[67 empty] | Air cooled, with condenser, electrically operated | 2.8 | [31 empty] | 4 | 24 | 120 | -0.46019 | 0.0068885 | -1.0146e-05 | 0.36839 | -0.0050828 | 7.4915e-06 | CDD | [49 empty] | Summerside | Île-du-Prince-Édouard | Summerside | P.E.I.
[67 empty] | Air cooled, without condenser, electrically operated | 3.1 | [31 empty] | 4 | 25 | 121 | 0.0073737 | 1.5101e-05 | -1.322e-09 | 0.0029351 | -7.4896e-06 | 6.3088e-10 | HDD | [49 empty] | Medicine Hat | Alberta | Medicine Hat | Alberta
[67 empty] | Water cooled, electrically operated, positive displacement (reciprocating) | 4.2 | [31 empty] | 4 | 26 | 122 | -0.024443 | 0.00072382 | -9.6633e-07 | 0.0084599 | -0.00026473 | 3.5286e-07 | CDD | [49 empty] | Moncton | Nouveau-Brunswick | Moncton | New Brunswick
[67 empty] | Water cooled, electrically operated, positive displacement (rotary screw and scroll) < 150 Tons | 4.45 | [31 empty] | 4 | 27 | 123 | -68.7122 | 0.023008 | -1.6446e-06 | 43.1095 | -0.014179 | 1.0085e-06 | HDD | [49 empty] | Mount Forest | Ontario | Mount Forest | Ontario
[67 empty] | Water cooled, electrically operated, positive displacement (rotary screw and scroll) >= 150 Tons & < 300 Tons | 4.9 | [31 empty] | 4 | 28 | 124 | -2.5881 | 0.026476 | -3.9394e-05 | 1.6178 | -0.012157 | 1.8289e-05 | CDD | [49 empty] | Saint-John | Nouveau-Brunswick | Saint John | New Brunswick
[67 empty] | Water cooled, electrically operated, positive displacement (rotary screw and scroll) >= 300 Tons | 5.5 | [31 empty] | 4 | 29 | 125 | 34.3223 | -0.011516 | 8.7598e-07 | -17.2003 | 0.0060139 | -4.6421e-07 | HDD | [49 empty] | St. John's | Terre-Neuve | St John's | Newfoundland
[67 empty] | Water cooled, electrically operated, positive displacement (centrifugal) < 150 Tons | 5 | [31 empty] | 4 | 30 | 126 | 0.96503 | 0.018504 | -4.4272e-05 | -0.77794 | -0.0062778 | 2.0366e-05 | CDD | [49 empty] | Sherbrooke | Québec | Sherbrooke | Quebec
[67 empty] | Water cooled, electrically operated, positive displacement (centrifugal) >= 150 Tons & < 300 Tons | 5.55 | [31 empty] | 4 | 31 | 127 | 83.3521 | -0.021305 | 9.241e-07 | -81.0455 | 0.021001 | -9.1522e-07 | HDD | [49 empty] | Stephenville | Terre-Neuve | Stephenville | Newfoundland
[67 empty] | Water cooled, electrically operated, positive displacement (centrifugal) >= 300 Tons | 6.1 | [31 empty] | 4 | 32 | 128 | -1.2037 | 0.019564 | -3.2141e-05 | 0.87219 | -0.010963 | 2.0465e-05 | CDD | [49 empty] | Williams Lake | Colombie Brit. | Williams Lake | Br. Columbia
[67 empty] | Air cooled absorption single effect | 0.6 | [31 empty] | 5 | 1 | 129 | 1.0637 | -0.00016573 | 7.6993e-09 | -0.55193 | 8.166e-05 | -3.597e-09 | HDD | [49 empty] | Sault Ste. Marie | Ontario | Sault Ste. Marie | Ontario
[67 empty] | Water cooled absorption single effect | 0.7 | [31 empty] | 5 | 2 | 130 | 0.70667 | -0.00010365 | 4.4243e-09 | -0.25498 | 3.3238e-05 | -1.1874e-09 | HDD | [49 empty] | Calgary | Alberta | Calgary | Alberta
[67 empty] | Absorption double effect, indirect-fired | 1 | [31 empty] | 5 | 3 | 131 | 0.57118 | -6.057e-05 | 1.585e-09 | -0.49739 | 5.0528e-05 | -1.1777e-09 | HDD | [49 empty] | Gander | Terre-Neuve | Gander | Newfoundland
[67 empty] | Absorption double effect, direct-fired | 1 | [31 empty] | 5 | 4 | 132 | 0.27563 | -3.0383e-05 | 8.5518e-10 | -0.11996 | 1.2735e-05 | -3.2266e-10 | HDD | [49 empty] | Québec | Québec | Quebec | Quebec
[100 empty] | 5 | 5 | 133 | -2.3516 | 0.00074624 | -6.3232e-08 | 2.5583 | -0.00074907 | 5.9004e-08 | HDD | [49 empty] | Prince George | Colombie Brit. | Prince George | Br. Columbia
[100 empty] | 5 | 6 | 134 | 0.14331 | 2.3963e-05 | -3.3826e-09 | 0.84522 | -0.00023414 | 1.6335e-08 | TDD | [49 empty] | North Bay | Ontario | North Bay | Ontario
[100 empty] | 5 | 7 | 135 | -0.072656 | 1.4214e-05 | -7.8801e-10 | 0.0025076 | -6.3482e-07 | 4.0319e-11 | HDD | [49 empty] | Edmonton | Alberta | Edmonton | Alberta
[100 empty] | 5 | 8 | 136 | 0.012468 | -2.1222e-06 | 1.1877e-10 | -0.0010916 | 1.6803e-07 | -8.9154e-12 | TDD | [49 empty] | Sudbury | Ontario | Sudbury | Ontario
[100 empty] | 5 | 9 | 137 | -0.0716 | 9.4066e-06 | -3.5993e-10 | 0.0040551 | -8.2134e-07 | 4.2502e-11 | HDD | [49 empty] | Estevan | Saskatchewan | Estevan | Saskatchewan
[100 empty] | 5 | 10 | 138 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Swift Current | Saskatchewan | Swift Current | Saskatchewan
[100 empty] | 5 | 11 | 139 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Mont Joli | Québec | Mont Joli | Quebec
[100 empty] | 5 | 12 | 140 | 0.77426 | -3.7723e-05 | 7.5114e-09 | 0 | 0 | 0 | HDD | [49 empty] | Charlo (Campbellton) | Nouveau-Brunswick | Charlo (Campbellton) | New Brunswick
[100 empty] | 5 | 13 | 141 | -0.0028694 | 0.00046249 | -4.8023e-07 | 0.00021599 | -4.2588e-05 | 4.4872e-08 | CDD | [49 empty] | Rivière-du-Loup | Québec | Riviere-du-Loup | Quebec
[100 empty] | 5 | 14 | 142 | -0.001629 | -0.020964 | 2.6796e-05 | -2.6867 | 0.08055 | -0.00010496 | CDD | [49 empty] | Thunder Bay | Ontario | Thunder Bay | Ontario
[100 empty] | 5 | 15 | 143 | 0.044874 | 0.0010143 | -1.7297e-06 | -0.02987 | -0.00054246 | 9.4056e-07 | CDD | [49 empty] | Red Deer | Alberta | Red Deer | Alberta
[100 empty] | 5 | 16 | 144 | 0.051124 | -0.00087868 | 1.2464e-06 | 0.13985 | 0.00015217 | -3.3671e-07 | CDD | [49 empty] | Regina | Saskatchewan | Regina | Saskatchewan
[67 empty] | French | English | [31 empty] | 5 | 17 | 145 | -0.071591 | 2.0794e-05 | 1.4113e-09 | 0.085843 | -3.0183e-05 | 4.8461e-10 | HDD | [49 empty] | Bagotville | Québec | Bagotville | Quebec
[67 empty] | Thermopompes et conditionneurs d'air autonomes refroidis à l'air et commandés par moteur électirque | Air Cooled Unitary Central Air-Conditioners and Heat Pumps - Electrically Operated | [31 empty] | 5 | 18 | 146 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Kenora | Ontario | Kenora | Ontario
[67 empty] | Conditionneurs d'air (CAVM) et thermopompes (TVM) verticaux monoblocs | Single-Package Vertical Air Conditioners (SPVAC) and Heat Pumps (SPVHP) | [31 empty] | 5 | 19 | 147 | 0.084051 | -2.1983e-05 | 1.5188e-09 | -0.0061717 | 1.6722e-06 | -1.1546e-10 | HDD | [49 empty] | Winnipeg | Manitoba | Winnipeg | Manitoba
[67 empty] | Thermopompes et conditionneurs d'air autonomes refroidis par évaporation ou par eau et par évaporation, et commandés par moteur électirque | Evaporatively Cooled and Water Evaporatively Cooled Unitary Air Conditioners and Heat Pumps - Electically Operated | [31 empty] | 5 | 20 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Saskatoon | Saskatchewan | Saskatoon | Saskatchewan
[67 empty] | Groupes condenseur-compresseur | Condensing Units | [31 empty] | 5 | 21 | 149 | -0.00013614 | -2.3551e-08 | 1.4939e-12 | 1.831e-07 | -5.568e-11 | 6.3138e-15 | HDD | [49 empty] | Grande Prairie | Alberta | Grande Prairie | Alberta
[67 empty] | Thermopompes et conditionneurs d'air autonomes refroidis par eau et par évaporation et commandés par moteur électirque | Water-Cooled Unitary Air Conditioners and Heat Pumps - Electrically Operated | [31 empty] | 5 | 22 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Fort St. John | Colombie Brit. | Fort St. John | Br. Columbia
[67 empty] | Thermopompes géothermiques à expansion directe commandées par moteur électrique | Direct-expansion ground-source heat pumps <= 21 (71700) | [31 empty] | 5 | 23 | 151 | 0.037566 | 8.3265e-06 | -6.2238e-10 | -0.021588 | -4.3036e-06 | 3.2043e-10 | HDD | [49 empty] | Brandon | Manitoba | Brandon | Manitoba
[67 empty] | Conditionneurs d'air (CAIL) et thermopompes (TIL) intégrés locaux | Packaged Terminal Air Conditioners (PTAC) and Heat Pumps (PTHP) | [31 empty] | 5 | 24 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Dauphin | Manitoba | Dauphin | Manitoba
[67 empty] | Climatiseurs de pièce et climatiseurs/thermopompes | Room Air Conditioners and Room Air Conditioner Heat Pumps | [31 empty] | 5 | 25 | 153 | 0.0030746 | 1.3939e-05 | -1.0721e-09 | 0.00235 | -6.494e-06 | 5.0265e-10 | HDD | [49 empty] | Timmins | Ontario | Timmins | Ontario
[67 empty] | Conditionneurs d'air de salle d'ordinateurs | Computer Room Air Conditioners | [31 empty] | 5 | 26 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Sept-Îles | Québec | Sept-Iles | Quebec
[67 empty] | Refroidisseurs à eau monobloc | Packaged Water Chillers | [31 empty] | 5 | 27 | 155 | -115.7603 | 0.042982 | -3.5253e-06 | 71.0899 | -0.026112 | 2.1365e-06 | HDD | [49 empty] | Val d'Or | Québec | Val d'Or | Quebec
[100 empty] | 5 | 28 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Battle Harbour (St Anthony) | Terre-Neuve | Battle Harbour (St Anthony) | Newfoundland
[100 empty] | 5 | 29 | 157 | 82.428 | -0.023289 | 1.5709e-06 | -48.3704 | 0.013863 | -9.3821e-07 | HDD | [49 empty] | Peace River | Alberta | Peace River | Alberta
[100 empty] | 5 | 30 | 158 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Kapuskasing | Ontario | Kapuskasing | Ontario
[100 empty] | 5 | 31 | 159 | -108.3751 | 0.041618 | -3.5373e-06 | 107.645 | -0.040975 | 3.484e-06 | HDD | [49 empty] | Prince Albert | Saskatchewan | Prince Albert | Saskatchewan
[100 empty] | 5 | 32 | 160 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Fort McMurray | Alberta | Fort McMurray | Alberta
[100 empty] | 6 | 1 | 161 | 0.14829 | 6.3151e-05 | -4.0163e-09 | -0.10817 | -3.6287e-05 | 2.138e-09 | HDD | [49 empty] | Cartwright (Happy Valley - Goose Bay) | Terre-Neuve | Cartwright (Happy Valley - Goose Bay) | Newfoundland
[100 empty] | 6 | 2 | 162 | 0.083226 | 3.7136e-05 | -2.3847e-09 | -0.035847 | -1.2754e-05 | 7.5671e-10 | HDD | [49 empty] | Happy Valley - Goose Bay | Terre-Neuve | Happy Valley - Goose Bay | Newfoundland
[100 empty] | 6 | 3 | 163 | -0.086902 | 0.00017566 | -1.3097e-08 | 0.12756 | -0.00028416 | 2.1064e-08 | HDD | [49 empty] | The Pas | Manitoba | The Pas | Manitoba
[67 empty] | Sub-Systems | [32 empty] | 6 | 4 | 164 | -0.021112 | 4.5075e-05 | -3.3752e-09 | 0.0079073 | -1.9369e-05 | 1.4412e-09 | HDD | [49 empty] | Whitehorse | Yukon | Whitehorse | Yukon
[100 empty] | 6 | 5 | 165 | -6.0072 | 0.0017935 | -1.433e-07 | 4.3095 | -0.0012089 | 9.7195e-08 | HDD | [49 empty] | Whitehorse | Yukon | Whitehorse | Yukon
[63 empty] | 4.395 | SEER | Air Cooled Unitary Central Air-Conditioners and Heat Pumps - Electrically Operated | Thermopompes et conditionneurs d'air autonomes refroidis à l'air et commandés par moteur électrique | Systeme biblocs <= 19 (65000) | Split System <= 19 (65000) | 1 | [30 empty] | 6 | 6 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Fort Nelson | Colombie Brit. | Fort Nelson | Br. Columbia
[63 empty] | 4.102 | SEER |  |  | System monoblocs <= 19 (65000) | Single-package systems <= 19 (65000) | 1 | [30 empty] | 6 | 7 | 167 | -0.0032529 | -6.3072e-06 | 4.6773e-10 | -0.00019131 | 3.695e-07 | -3.2232e-11 | TDD | [49 empty] | Big Trout Lake | Ontario | Big Trout Lake | Ontario
[63 empty] | 2.8421 | EER |  |  | Toutes les phases > 19 (65000) et < 73 (250000) | All phases > 19 (65000) and < 73 (250000) | 1 | [30 empty] | 6 | 8 | 168 | -4.9299e-05 | 1.6688e-07 | 3.2534e-10 | 1.1825e-05 | -3.4537e-08 | -2.0529e-11 | CDD | [49 empty] | Fort Smith | Territoires du N.O. | Fort Smith | Northwest Terr.
[63 empty] | 3.28 | COP |  |  | Conditionneurs d'air, toutes les phases, systemes biblocs et monoblocs >= 19 kW et , 40 kW, section de chauffage a resistance electrique | Air conditioners, all phases, split and single package >= 19 kW and < 40 kW, electric resistance heating section | 1 | [30 empty] | 6 | 9 | 169 | 0.010446 | -1.475e-05 | 1.0789e-09 | 8.9451e-05 | 6.3224e-07 | -5.1777e-11 | TDD | [49 empty] | Thompson | Manitoba | Thompson | Manitoba
[63 empty] | 3.22 | COP |  |  | Conditionneurs d'air, toutes les phases, systemes biblocs et monoblocs >= 19 kW et , 40 kW, autre section de chauffage | Air conditioners, all phases, split and single package >= 19 kW and < 40 kW, other heating section | 1 | [30 empty] | 6 | 10 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Uranium City | Saskatchewan | Uranium City | Saskatchewan
[63 empty] | 3.22 | COP |  |  | Conditionneurs d'air, toutes les phases, systemes biblocs et monoblocs >= 40 kW et , 70 kW, section de chauffage a resistance electrique | Air conditioners, all phases, split and single package >= 40 kW and < 70 kW, electric resistance heating section | 1 | [30 empty] | 6 | 11 | 171 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Wabush | Terre-Neuve | Wabush | Newfoundland
[63 empty] | 3.16 | COP |  |  | Conditionneurs d'air, toutes les phases, systemes biblocs et monoblocs >= 40 kW et , 70 kW, autre section de chauffage | Air conditioners, all phases, split and single package >= 40 kW and < 70 kW, other heating section | 1 | [30 empty] | 6 | 12 | 172 | 0.17301 | 4.6877e-05 | 1.4757e-10 | 0 | 0 | 0 | HDD | [49 empty] | Nitchequon | Québec | Nitchequon | Quebec
[63 empty] | 2.93 | COP |  |  | Conditionneurs d'air, toutes les phases, systemes biblocs et monoblocs >= 70 kW et , 223 kW, section de chauffage a resistance electric | Air conditioners, all phases, split and single package >= 70 kW and < 223 kW, electric resistance heating section | 1 | [30 empty] | 6 | 13 | 173 | 0.039018 | -2.6657e-05 | 1.1004e-07 | -0.0036785 | 2.7637e-06 | -1.0257e-08 | CDD | [49 empty] | Kuujjuarapik | Québec | Kuujjuarapik | Quebec
[63 empty] | 2.87 | COP |  |  | Conditionneurs d'air, toutes les phases, systemes biblocs et monoblocs >= 70 kW et ,223 kW, section de chauffage a resistance electric | Air conditioners, all phases, split and single package >= 70 kW and < 223 kW, electric resistance heating section | 1 | [30 empty] | 6 | 14 | 174 | -0.34044 | -0.0026007 | 2.3746e-06 | -0.3802 | 0.0077964 | -7.6076e-06 | CDD | [49 empty] | Schefferville | Québec | Schefferville | Quebec
[63 empty] | 2.84 | COP |  |  | Conditionneurs d'air, toutes les phases, systemes biblocs et monoblocs >= 223 kW et < 22 kW, section de chauffage a resistance electric | Air conditioners, all phases, split and single package >= 223 kW, electric resistance heating section | 1 | [30 empty] | 6 | 15 | 175 | 0.0629 | -1.2843e-05 | 8.2094e-10 | 0.084753 | -2.1064e-05 | 1.6337e-09 | TDD | [49 empty] | Yellowknife | Territoires du N.O. | Yellowknife | Northwest Terr.
[63 empty] | 2.78 | COP |  |  | Air-cooled unitary air-conditioner, all phases, split and single package >= 223 kW, other heating section | Air conditioners, all phases, split and single package >= 223 kW, other heating section | 1 | [30 empty] | 6 | 16 | 176 | -0.15277 | 0.00017483 | -1.5918e-07 | 0.18559 | -0.00021053 | 1.9078e-07 | CDD | [49 empty] | Kuujuaq | Québec | Kuujuaq | Quebec
[63 empty] | 3.22 | COP |  |  | Thermopompes >= 19 kW et , 40 kW, section de chauffage a resistance electrique monobloc et bibloc | Heat Pumps >= 19 kW and < 40 kW, electric resistance heating section, split and single | 1 | [30 empty] | 6 | 17 | 177 | 0.011738 | 2.3161e-06 | -1.8822e-10 | -0.0072616 | -2.8321e-06 | 2.423e-10 | HDD | [49 empty] | Norman Wells | Territoires du N.O. | Norman Wells | Northwest Terr.
[63 empty] | 3.16 | COP |  |  | Thermopompes >= 19 kW et , 40 kW, autre section de chauffage, monobloc et bibloc | Heat Pumps >= 19 kW and < 40 kW, other heating section, split and single | 1 | [30 empty] | 6 | 18 | 178 | 0 | 0 | 0 | 0 | 0 | 0 | CDD | [49 empty] | Churchill | Manitoba | Churchill | Manitoba
[63 empty] | 3.1 | COP |  |  | Thermopompes >= 40 kW et , 70 kW,section de chauffage a resistance electrique monobloc et bibloc | Heat Pumps >= 40 kW and < 70 kW, electric resistance heating section, split and single | 1 | [30 empty] | 6 | 19 | 179 | 8.883e-05 | 4.3307e-07 | -2.4761e-11 | -0.00014425 | 4.4813e-08 | -4.6748e-12 | HDD | [49 empty] | Inuvik | Territoires du N.O. | Inuvik | Northwest Terr.
[63 empty] | 3.04 | COP |  |  | Thermopompes >= 40 kW et , 70 kW, section de chauffage a resistance electrique monobloc et bibloc | Heat Pumps >= 40 kW and < 70 kW, otherheating section, split and single | 1 | [30 empty] | 6 | 20 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Iqualuit | Nunavut | Iqualuit | Nunavut
[63 empty] | 2.78 | COP |  |  | Thermopompes >= 70 kW, electric resistance heating section, split et single | Heat Pumps >= 70 kW, electric resistance heating section, split and single | 1 | [30 empty] | 6 | 21 | 181 | -1.484e-05 | -2.189e-08 | 1.4555e-12 | -1.6919e-07 | 8.4824e-11 | -6.9094e-15 | HDD | [49 empty] | Inuvik (NWT) | Yukon | Inuvik (NWT) | Yukon
[63 empty] | 2.72 | COP |  |  | Thermopompes >= 70 kW, other heating section, split et single | Heat Pumps >= 70 kW, other heating section, split and single | 1 | [30 empty] | 6 | 22 | 182 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Chesterfield Inlet | Nunavut | Chesterfield Inlet | Nunavut
[63 empty] | 3.3 | COP |  |  | Thermopompes >= 19 kW et , 70 kWen mode de refroidissement a une temp. de 8.3 ⁰C db / 6.1 ⁰C wb | Heat Pumps >= 19 kW and < 70 kW in cooling mode at 8.3 ⁰C db / 6.1 ⁰C wb | 1 | [30 empty] | 6 | 23 | 183 | 0.0089553 | 4.2629e-06 | -2.5266e-10 | -0.0046748 | -2.4543e-06 | 1.4845e-10 | HDD | [49 empty] | Coral Harbour | Nunavut | Coral Harbour | Nunavut
[63 empty] | 2.25 | COP |  |  | Thermopompes >= 19 kW et , 70 kW en mode de refroidissement a une temp. de 8.3 ⁰C db / -9.4 ⁰C wb | Heat Pumps >= 19 kW and < 70 kW in cooling mode at 8.3 ⁰C db / -9.4 ⁰C wb | 1 | [30 empty] | 6 | 24 | 184 | 0 | 0 | 0 | 0 | 0 | 0 | HDD | [49 empty] | Cambridge Bay | Nunavut | Cambridge Bay | Nunavut
[63 empty] | 3.2 | COP |  |  | Thermopompes >= 70 kW ien mode de refroidissement a une temp. de at 8.3 ⁰C db / -6.1 ⁰C wb | Heat Pumps >= 70 kW in cooling mode at 8.3 ⁰C db / 6.1 ⁰C wb | 1 | [30 empty] | 6 | 25 | 185 | 0.0030566 | 4.5454e-06 | -3.3914e-10 | -0.00020818 | -2.1136e-06 | 1.6717e-10 | HDD
[63 empty] | 2.05 | COP |  |  | Thermopompes >= 70 kW en mode refroidissement a une temp. de 8.3 ⁰C db / -9.4 ⁰C wb | Heat Pumps >= 70 kW in cooling mode at 8.3 ⁰C db / -9.4 ⁰C wb | 1 | [30 empty] | 6 | 26 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[63 empty] | 2.93 | EER | Single-Package Vertical Air Conditioners (SPVAC) and Heat Pumps (SPVHP) | Single-Package Vertical Air Conditioners (SPVAC) and Heat Pumps (SPVHP) | CAVM et TVM en mode de refroidissement < 19 kW | SPVAC and SPVHP in cooling mode < 19 kW | 2 | [30 empty] | 6 | 27 | 187 | 1384.682 | -0.50447 | 4.0929e-05 | -875.7517 | 0.31934 | -2.5913e-05 | HDD
[63 empty] | 2.7835 | EER |  |  | CAVM et TVM en mode de refroidissement >= 19 kW et , 40 kW | SPVAC and SPVHP in cooling mode >= 19 kW and < 40 kW | 2 | [30 empty] | 6 | 28 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[63 empty] | 2.5198 | EER |  |  | CAVM et TVM en mode de refroidissement >= 40 kW et , 70 kW | SPVAC and SPVHP in cooling mode >= 40 kW and < 70 kW | 2 | [30 empty] | 6 | 29 | 189 | -19.3774 | 0.0056624 | -4.3651e-07 | 11.9771 | -0.0034351 | 2.6366e-07 | HDD
[63 empty] | 3.1 | COP |  |  | TVM en mode de chauffage < 19 kW | SPVHP in heating mode < 19 kW | 2 | [30 empty] | 6 | 30 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[63 empty] | 3 | COP |  |  | TVM en mode de chauffage >= 19 kW et < 40 kW | SPVHP in heating mode >= 19 kW and < 40 kW | 2 | [30 empty] | 6 | 31 | 191 | -95.1262 | 0.039818 | -3.6708e-06 | 95.0443 | -0.039444 | 3.6424e-06 | HDD
[63 empty] | 2.9 | COP |  |  | TVM en mode de chauffage >= 40 kW et < 70 kW | SPVHP in heating mode >= 40 kW and < 70 kW | 2 | [30 empty] | 6 | 32 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[63 empty] | 3.54 | COP | Evaporatively Cooled and Water Evaporatively Cooled Unitary Air Conditioners and Heat Pumps - Electically Operated | Evaporatively Cooled and Water Evaporatively Cooled Unitary Air Conditioners and Heat Pumps - Electically Operated | Refroidissement par evaporation <= 19 (65000) | Evaporatively cooled <= 19 (65000) | 3 | [30 empty] | 7 | 1 | 193 | 0.82221 | 2.9702e-05 | -5.0895e-09 | -0.37313 | -2.8642e-05 | 3.2216e-09 | HDD
[63 empty] | 3.37 | COP |  |  | Refroidissement par evaporation ou par eau et evaporation, biblocs et monoblocs >= 19 kW et < 40 kW section de chauffage a resistance electrique | Evaporatively cooled and water evaporatively cooled, split and single-package >= 19 kW and < 40 kW electric resistance heating section | 3 | [30 empty] | 7 | 2 | 194 | 0.53419 | 3.1491e-05 | -4.2319e-09 | -0.17217 | -1.7114e-05 | 1.7555e-09 | TDD
[63 empty] | 3.31 | COP |  |  | Refroidissement par evaporation ou par eau et evaporation, biblocs et monoblocs >= 19 kW et < 40 kW autre section de chauffage | Evaporatively cooled and water evaporatively cooled, split and single-package >= 19 kW and < 40 kW other heating section | 3 | [30 empty] | 7 | 3 | 195 | 0.63425 | 3.8563e-05 | -5.4431e-09 | -0.55547 | -2.8938e-05 | 4.2565e-09 | TDD
[63 empty] | 3.22 | COP |  |  | Refroidissement par evaporation ou par eau et evaporation, biblocs et monoblocs >= 40 kW et < 70 kW section de chauffage a resistance electrique | Evaporatively cooled and water evaporatively cooled, split and single-package >= 40 kW and < 70 kW electric resistance heating section | 3 | [30 empty] | 7 | 4 | 196 | 0.31239 | 1.3961e-05 | -2.3002e-09 | -0.13056 | -7.2788e-06 | 1.0523e-09 | HDD
[63 empty] | 3.16 | COP |  |  | Refroidissement par evaporation ou par eau et evaporation, biblocs et monoblocs >= 40 kW et < 70 kW autre section de chauffage | Evaporatively cooled and water evaporatively cooled, split and single-package >= 40 kW and < 70 kW other heating section | 3 | [30 empty] | 7 | 5 | 197 | -2.5473 | 0.00097053 | -8.0799e-08 | 2.1212 | -0.00072533 | 5.8471e-08 | HDD
[63 empty] | 3.22 | COP |  |  | Refroidissement par eau et evaporation, conditionneurs d'air, biblocs et monoblocs >= 70 kW section de chauffage a resistance electrique | Water evaporatively cooled air conditioners, split and single-packaged >= 70 kW electric resistance heating section | 3 | [30 empty] | 7 | 6 | 198 | 0.11488 | 1.0911e-07 | -5.6992e-10 | -0.157 | 3.9986e-06 | 3.9155e-10 | TDD
[63 empty] | 3.16 | COP |  |  | Refroidissement par eau et evaporation, conditionneurs d'air, biblocs et monoblocs >= 70 kW autre section de chauffage | Water evaporatively cooled air conditioners, split and single-packaged >= 70 kW other heating section | 3 | [30 empty] | 7 | 7 | 199 | -0.09819 | 8.3937e-06 | -1.2968e-10 | 0.0055369 | -8.423e-07 | 3.0904e-11 | HDD
[63 empty] | 11.2 |  |  |  | Climatiseur, refroidi par air, section électrique ou sans chauffage - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, >=19 <40 kW | Air conditioner, air-cooled, electric or no heating - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, >=19 <40 kW | 4 | [30 empty] | 7 | 8 | 200 | -0.00012857 | 8.9696e-08 | -7.6748e-12 | 0 | 0 | 0 | HDD
[63 empty] | 11 |  |  |  | Climatiseur, refroidi par air, section électrique ou sans chauffage - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, ≥ 39.6 < 70.3 kW | Air conditioner, air-cooled, electric or no heating - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, ≥ 39.6 < 70.3 KW | 4 | [30 empty] | 7 | 9 | 201 | -0.10466 | -4.1253e-07 | 5.9279e-10 | 0.01465 | -1.7109e-06 | 3.2321e-11 | TDD
[63 empty] | 10 |  |  |  | Climatiseur, refroidi par air, section électrique ou sans chauffage - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, ≥ 70.3 < 223 kW | Air conditioner, air-cooled, electric or no heating - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, ≥ 70.3 < 223 kW | 4 | [30 empty] | 7 | 10 | 202 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[63 empty] | 9.7 |  |  |  | Climatiseur, refroidi par air, section électrique ou sans chauffage - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, >= 223 kW | Air conditioner, air-cooled, electric or no heating - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, >= 223 kW | 4 | [30 empty] | 7 | 11 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[63 empty] | 11.5 |  |  |  | Climatiseur, refroidi par eau et par évaporation, section électrique ou sans chauffage - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB, ≥ 19.0 < 39.6 kW | Air conditioner, water & evaporatively cooled, electric or no heating - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB, ≥ 19.0 < 39.6 kW | 4 | [30 empty] | 7 | 12 | 204 | 0.17203 | 7.8956e-05 | -4.4579e-10 | 0 | 0 | 0 | HDD
[63 empty] | 11 |  |  |  | Climatiseur, refroidi par eau et par évaporation, section électrique ou sans chauffage - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB, ≥ 39.6 < 70.3 kW | Air conditioner, water & evaporatively cooled, electric or no heating - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB, ≥ 39.6 < 70.3 kW | 4 | [30 empty] | 7 | 13 | 205 | -0.003661 | 0.00026962 | -2.9283e-07 | 0.00018553 | -1.6533e-05 | 1.8059e-08 | CDD
[63 empty] | 11 |  |  |  | Climatiseur, refroidi par eau et par évaporation, section électrique ou sans chauffage - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB, ≥ 70.3 kW | Air conditioner, water & evaporatively cooled, electric or no heating - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB, ≥ 70.3 kW | 4 | [30 empty] | 7 | 14 | 206 | 0.06104 | -0.0013809 | 1.4317e-06 | 0.30514 | -0.0026206 | 3.1852e-06 | CDD
[63 empty] | 11 |  |  |  | Thermopompe, section électrique ou sans chauffage - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB, ≥ 19.0 < 39.6 kW | Heat pump, electric or no heating - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB, ≥ 19.0 < 39.6 kW | 4 | [30 empty] | 7 | 15 | 207 | 0.064553 | -0.0001863 | 1.8935e-07 | -0.051471 | 0.00025164 | -3.0841e-07 | CDD
[63 empty] | 10.6 |  |  |  | Thermopompe, section électrique ou sans chauffage - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB, ≥ 39.6 < 70.3 kW | Heat pump, electric or no heating - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB, ≥ 39.6 < 70.3 kW | 4 | [30 empty] | 7 | 16 | 208 | -0.10413 | -0.00013205 | 6.3055e-09 | 0.084017 | 0.00019234 | -1.0577e-08 | TDD
[63 empty] | 9.5 |  |  |  | Thermopompe, section électrique ou sans chauffage - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB, ≥ 70.3 kW | Heat pump, electric or no heating - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB, ≥ 70.3 kW | 4 | [30 empty] | 7 | 17 | 209 | 0.0098722 | -5.2042e-06 | 8.3825e-10 | 0 | 0 | 0 | TDD
[63 empty] | 11 |  |  |  | Climatiseur, refroidi par air, toutes les autres sections avec chauffage - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, >=19 <40 | Air conditioner, air-cooled, all other heating section - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, >=19 <40 | 4 | [30 empty] | 7 | 18 | 210 | -0.012265 | 3.5782e-05 | -4.8998e-08 | 0.014898 | 4.6681e-07 | -1.2801e-11 | CDD
[63 empty] | 10.8 |  |  |  | Climatiseur, refroidi par air, toutes les autres sections avec chauffage - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB | Air conditioner, air-cooled, all other heating section - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB | 4 | [30 empty] | 7 | 19 | 211 | 0.035668 | -7.431e-06 | 4.8856e-10 | -0.0024622 | 5.2828e-07 | -3.4859e-11 | HDD
[63 empty] | 9.8 |  |  |  | Climatiseur, refroidi par air, toutes les autres sections avec chauffage - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB | Air conditioner, air-cooled, all other heating section - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB | 4 | [30 empty] | 7 | 20 | 212 | 0.00025572 | 2.1417e-06 | -3.2965e-09 | -1.9579e-05 | -5.8945e-08 | 8.5778e-11 | CDD
[63 empty] | 9.5 |  |  |  | Climatiseur, refroidi par air, toutes les autres sections avec chauffage - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, >= 223 kW | Air conditioner, air-cooled, all other heating section - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB, >= 223 kW | 4 | [30 empty] | 7 | 21 | 213 | -6.3593e-05 | -1.5951e-08 | 4.1115e-13 | -1.5325e-09 | 1.1579e-11 | -4.5392e-16 | HDD
[63 empty] | 11.3 |  |  |  | Climatiseur, refroidi par eau et par évaporation, toutes les autres sections avec chauffage - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | Air conditioner, water & evaporatively cooled, all other heating section - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | 4 | [30 empty] | 7 | 22 | 214 | 1.2018e-05 | -8.2575e-07 | 9.0512e-10 | 1.0801e-07 | -1.3035e-09 | 2.33e-12 | CDD
[63 empty] | 10.8 |  |  |  | Climatiseur, refroidi par eau et par évaporation, toutes les autres sections avec chauffage - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | Air conditioner, water & evaporatively cooled, all other heating section - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | 4 | [30 empty] | 7 | 23 | 215 | 0.0058897 | 9.0991e-06 | -4.6926e-10 | 0.00025456 | -6.2738e-06 | 3.5566e-10 | HDD
[63 empty] | 10.8 |  |  |  | Climatiseur, refroidi par eau et par évaporation, toutes les autres sections avec chauffage - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | Air conditioner, water & evaporatively cooled, all other heating section - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | 4 | [30 empty] | 7 | 24 | 216 | -0.0091481 | 0.000218 | -2.4578e-07 | 0.0063893 | -0.00012906 | 1.4365e-07 | CDD
[63 empty] | 10.8 |  |  |  | Thermopompe, toutes les autres sections avec chauffage - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | Heat pump, all other heating section - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | 4 | [30 empty] | 7 | 25 | 217 | 0.020656 | 1.2697e-07 | 1.7731e-10 | -0.0094362 | 6.1969e-07 | -1.2368e-10 | HDD
[63 empty] | 10.4 |  |  |  | Thermopompe, toutes les autres sections avec chauffage - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | Heat pump, all other heating section - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | 4 | [30 empty] | 7 | 26 | 218 | -0.0036323 | 0.00010835 | -1.1617e-07 | 0.0016415 | -4.0794e-05 | 4.1859e-08 | CDD
[63 empty] | 9.3 |  |  |  | Thermopompe, toutes les autres sections avec chauffage - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | Heat pump, all other heating section - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | 4 | [30 empty] | 7 | 27 | 219 | -288.0561 | 0.10699 | -8.8291e-06 | 178.2718 | -0.065967 | 5.4418e-06 | HDD
[63 empty] | 10.1 |  |  |  | Groupes compresseur-condenseur - RCU-A | Large condensing units - RCU-A | 4 | [30 empty] | 7 | 28 | 220 | 334.3689 | -0.0043808 | -0.0012232 | -207.7281 | 0.0033963 | 0.00076058 | CDD
[63 empty] | 13.1 |  |  |  | Groupes compresseur-condenseur - RCU-E, RCU-W | Large condensing units - RCU-E, RCU-W | 4 | [30 empty] | 7 | 29 | 221 | 30.0687 | -0.0053735 | 2.2075e-07 | -17.452 | 0.0031603 | -1.2803e-07 | HDD
[63 empty] | 2.96 | COP |  |  | Refroidissement par air >= 73 (250000) | Condensing unit - Air-cooled >= 73 (250000) | 4 | [30 empty] | 7 | 30 | 222 | -14.5413 | 0.09178 | -0.00011556 | 9.2396 | -0.054362 | 6.8214e-05 | CDD
[63 empty] | 3.84 | COP |  |  | Refroidissement par eau et evaporation >= 73 (250000) | Condensing unit - Water evaporatively cooled >= 73 (250000) | 4 | [30 empty] | 7 | 31 | 223 | -47.3204 | 0.019389 | -1.7365e-06 | 47.3977 | -0.019105 | 1.7184e-06 | HDD
[63 empty] | 4.75 |  | Water-Cooled Unitary Air Conditioners and Heat Pumps - Electrically Operated | Water-Cooled Unitary Air Conditioners and Heat Pumps - Electrically Operated | Thermopompes geothermiques et a eau < 35 (119500) | Ground or water source heat pumps < 35 (119500) - open systems | 5 | [30 empty] | 7 | 32 | 224 | 0.0048544 | -0.00011449 | 1.3985e-07 | -0.0038603 | 0.00013657 | -1.6233e-07 | CDD
[63 empty] | 3.6 |  |  |  | Ground or water source heat pumps < 35 (119500) - closed systems | Ground or water source heat pumps < 35 (119500) - closed systems | 5 | [30 empty] | 8 | 1 | 225 | 0.79782 | 4.9917e-05 | -7.594e-09 | -0.44667 | -5.0522e-05 | 5.9758e-09 | HDD
[63 empty] | 3.52 |  |  |  | Thermopompes sur boucle d'eau < 40 (136500) | Internal water-loop heat pumps < 40 (136500) | 5 | [30 empty] | 8 | 2 | 226 | 0.46996 | 2.2623e-05 | -3.8238e-09 | -0.15938 | -1.3302e-05 | 1.6816e-09 | HDD
[63 empty] | 3.54 | COP |  |  | Conditionneurs d'air a refroidissement par eau < 19 (65000) | Water-cooled air conditioners < 19 (65000) | 5 | [30 empty] | 8 | 3 | 227 | 0.65575 | 6.1462e-05 | -7.406e-09 | -0.84914 | -8.1002e-05 | 9.5103e-09 | HDD
[63 empty] | 3.37 | COP |  |  | Conditionneurs d'air a refroidissement par eau >= 19 kW et < 40 kW chauffage a resistance electrique (ou aucun) | Water-cooled air conditioners >= 19 kW and < 40 kW electric resistance heating (or none) | 5 | [30 empty] | 8 | 4 | 228 | 0.20313 | 2.3433e-05 | -2.6769e-09 | -0.08446 | -1.1529e-05 | 1.2458e-09 | HDD
[63 empty] | 3.31 | COP |  |  | Water-cooled air conditioners >= 19 kW and < 40 kW all other | Water-cooled air conditioners >= 19 kW and < 40 kW all other | 5 | [30 empty] | 8 | 5 | 229 | -0.74312 | 0.0023314 | -1.3722e-06 | 0.49444 | -0.00068584 | -3.577e-07 | CDD
[63 empty] | 3.22 | COP |  |  | Conditionneurs d'air a refroidissement par eau >= 40 kW et < 70 kW chauffage a resistance electrique (ou aucun) | Water-cooled air conditioners >= 40 kW and < 70 kW electric resistance heating (or none) | 5 | [30 empty] | 8 | 6 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[63 empty] | 3.16 | COP |  |  | Conditionneurs d'air a refroidissement par eau >= 40 kW et < 70 kW tous les autres | Water-cooled air conditioners >= 40 kW and < 70 kW all other | 5 | [30 empty] | 8 | 7 | 231 | -0.095189 | 6.1271e-06 | 3.8645e-11 | 0.0073209 | -1.2881e-06 | 6.4662e-11 | TDD
[63 empty] | 3.22 | COP |  |  | Conditionneurs d'air a refroidissement par eau >= 70 kW chauffage a resistance electrique (ou aucun) | Water-cooled air conditioners >= 70 kW electric resistance heating (or none) | 5 | [30 empty] | 8 | 8 | 232 | -0.000799 | 1.1689e-06 | -9.8291e-11 | 0.00014834 | -1.4753e-07 | 1.2599e-11 | TDD
[63 empty] | 3.16 | COP |  |  | Conditionneurs d'air a refroidissement par eau >= 70 kW tous les autres | Water-cooled air conditioners >= 70 kW all other | 5 | [30 empty] | 8 | 9 | 233 | -0.08558 | -4.754e-06 | 8.0028e-10 | 0.016979 | -2.3169e-06 | 9.5043e-11 | TDD
[63 empty] | 3.809 |  | Direct-expansion ground-source heat pumps <= 21 (71700) | Direct-expansion ground-source heat pumps <= 21 (71700) | Thermopompes geothermiques a expansion directe <= 21 (71700) | Direct-expansion ground-source heat pumps <= 21 (71700) | 6 | [30 empty] | 8 | 10 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[63 empty] | -1 |  | Packaged Terminal Air Conditioners (PTAC) and Heat Pumps (PTHP) | Packaged Terminal Air Conditioners (PTAC) and Heat Pumps (PTHP) | CAIL et TIL refroidis par air et commandes par moteur electrique | PTAC and PTHP air-cooled electrically operated - Electrically Operated | 7 | [30 empty] | 8 | 11 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[63 empty] | -2 |  |  |  | TIL en mode de refroidissement standard | PTHP in cooling mode (Standard rating) | 7 | [30 empty] | 8 | 12 | 236 | 0.26333 | 4.6997e-05 | 1.5548e-09 | 0 | 0 | 0 | HDD
[63 empty] | -3 |  |  |  | TIL en mode de chauffage standard | PTHP in heating mode (Standard rating) | 7 | [30 empty] | 8 | 13 | 237 | 0.0039614 | 0.00025188 | -2.2345e-07 | -0.00043523 | -2.3164e-05 | 2.0888e-08 | CDD
[63 empty] | 2.4905 |  | Room Air Conditioners and Room Air Conditioner Heat Pumps | Room Air Conditioners and Room Air Conditioner Heat Pumps | Climatiseurs de piece a inversion de cycle avec volets lateraux < 10.55 (36000) | Room air conditioners with reserve cycle with louvered sides < 10.55 (36000) | 8 | [30 empty] | 8 | 14 | 238 | -0.21632 | -0.010515 | 1.2204e-05 | -2.0953 | 0.037565 | -4.3582e-05 | CDD
[63 empty] | 2.344 |  |  |  | Climatiseurs de piece a invversion de cycle sans volets lateraux < 10.55 (36000) | Room air conditioners with reserve cycle without louvered sides < 10.55 (36000) | 8 | [30 empty] | 8 | 15 | 239 | 0.054825 | 0.00035843 | -6.3362e-07 | -0.035005 | -0.00017299 | 3.2042e-07 | CDD
[63 empty] | 2.4905 |  |  |  | Climatiseurs de piece sans inversion de cycle < 10.55 (36000) | Room air conditioners without reverse cycle < 10.55 (36000) | 8 | [30 empty] | 8 | 16 | 240 | -0.089445 | 6.825e-06 | 2.0782e-10 | 0.057168 | 5.296e-06 | 1.0036e-10 | TDD
[63 empty] | 2.84 |  |  |  | Climatiseurs de piece avec volets lateraux < 1.8 kW | Room air conditioners with louvered sides < 1.8 kW | 8 | [30 empty] | 8 | 17 | 241 | 0.023801 | -1.4326e-05 | 2.4328e-09 | 0 | 0 | 0 | TDD
[63 empty] | 2.84 |  |  |  | Climatiseurs de piece avec volets lateraux >= 1.8 kW et < 2.3 kW | Room air conditioners with louvered sides >= 1.8 kW and < 2.3 kW | 8 | [30 empty] | 8 | 18 | 242 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[63 empty] | 2.87 |  |  |  | Climatiseurs de piece avec volets lateraux>= 2.3 kW et < 4.1 kW | Room air conditioners with louvered sides >= 2.3 kW and < 4.1 kW | 8 | [30 empty] | 8 | 19 | 243 | 0.012165 | -1.7453e-06 | 1.1512e-10 | -0.00061414 | 1.5483e-07 | -1.3289e-11 | TDD
[63 empty] | 2.84 |  |  |  | Climatiseurs de piece avec volets lateraux >= 4.1 kW et < 5.9 kW | Room air conditioners with louvered sides >= 4.1 kW and < 5.9 kW | 8 | [30 empty] | 8 | 20 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[63 empty] | 2.49 |  |  |  | Climatiseurs de piece avec volets lateraux >= 5.9 kW | Room air conditioners with louvered sides >= 5.9 kW | 8 | [30 empty] | 8 | 21 | 245 | -0.00023107 | 5.2675e-09 | 9.2263e-14 | -7.186e-08 | 1.159e-10 | -1.0965e-14 | HDD
[63 empty] | 2.64 |  |  |  | Climatiseurs de piece, sans volets lateraux < 2.3 kW | Room air conditioners without louvered sides < 2.3 kW | 8 | [30 empty] | 8 | 22 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[63 empty] | 2.49 |  |  |  | Climatiseurs de piece, sans volets lateraux >= 2.3 kW et < 5.9 kW | Room air conditioners wothout louvered sides >= 2.3 kW and < 5.9 kW | 8 | [30 empty] | 8 | 23 | 247 | 0.05858 | -8.9694e-07 | -4.9662e-12 | -0.028054 | -9.6738e-07 | 1.1373e-10 | HDD
[63 empty] | 2.49 |  |  |  | Climatiseurs de piece, sans volets lateraux >= 5.9 kW | Room air conditioners without louvered sides >= 5.9 kW | 8 | [30 empty] | 8 | 24 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[63 empty] | 2.65 |  |  |  | Thermopompes/ climatiseurs de piece avec volet lateraux < 5.9 kW | Room air conditioner heat pumps with louvered sides < 5.9 kW | 8 | [30 empty] | 8 | 25 | 249 | 0.038732 | 9.3228e-07 | -2.0537e-10 | -0.011352 | -1.5186e-06 | 1.7978e-10 | HDD
[63 empty] | 2.49 |  |  |  | Thermopompes/ climatiseurs de piece avec volet lateraux < 5.9 kW | Room air conditioner heat pumps with louvered sides < 5.9 kW | 8 | [30 empty] | 8 | 26 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[63 empty] | 2.49 |  |  |  | Thermopompes/ climatiseurs de piece sans volet lateraux < 5.9 kW | Room air conditioner heat pumps without louvered sides < 4.1 | 8 | [30 empty] | 8 | 27 | 251 | -235.5208 | 0.084671 | -6.6785e-06 | 145.6123 | -0.052053 | 4.0989e-06 | HDD
[63 empty] | 2.34 |  |  |  | Thermopomes/ climatiseurs de piece sans volet lateraux >= 4.1 | Room air conditioner heat pumps without louvered sides >= 4.1 | 8 | [30 empty] | 8 | 28 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[63 empty] | 2.55 |  |  |  | Climatiseurs de piece pour fenetre a battants seulement toutes les capacites | Room air conditioner casement only | 8 | [30 empty] | 8 | 29 | 253 | -68.8865 | 0.022075 | -1.6508e-06 | 43.5312 | -0.013727 | 1.0217e-06 | HDD
[63 empty] | 2.78 |  |  |  | Climatiseurs de piece pour feneetre a battants coulissante ou a guillotine toutes les capacites | Room air conditioner casement slider | 8 | [30 empty] | 8 | 30 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[63 empty] | 2.09 |  | Computer Room Air Conditioners | Computer Room Air Conditioners | Conditionneurs d'air, refroidis a l'air < 19 (65000) | Air-cooled < 19 (65000) | 9 | [30 empty] | 8 | 31 | 255 | 12.4013 | 0.0018052 | -6.9652e-07 | -10.9079 | -0.0018938 | 6.9528e-07 | HDD
[63 empty] | 1.99 |  |  |  | Conditionneurs d'air, refroidis a l'air < 19 (65000) et < 70 (240000) | Air-cooled < 19 (65000) and < 70 (240000) | 9 | [30 empty] | 8 | 32 | 256 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[63 empty] | 1.79 |  |  |  | Conditionneurs d'air, refroidis a l'air >= 70 (240000) | Air-cooled >= 70 (240000) | 9 | [30 empty] | 9 | 1 | 257 | 0.48776 | 8.6048e-05 | -9.4504e-09 | -0.22678 | -5.3976e-05 | 5.4601e-09 | HDD
[63 empty] | 2.49 |  |  |  | Conditionneurs d'air refroidis a l'eau < 19 (65000) | Water-cooled < 19 (65000) | 9 | [30 empty] | 9 | 2 | 258 | 0.31571 | 8.4483e-05 | -8.668e-09 | -0.097295 | -4.5166e-05 | 4.2612e-09 | HDD
[63 empty] | 2.39 |  |  |  | Conditionneurs d'air refroidis a l'eau >= 19 (65000) et < 70 (240000) | Water-cooled >= 19 (65000) and < 70 (240000) | 9 | [30 empty] | 9 | 3 | 259 | 0.23218 | 0.00013082 | -1.1458e-08 | -0.24165 | -0.00015112 | 1.3127e-08 | HDD
[63 empty] | 2.29 |  |  |  | Conditionneurs d'air refroidis a l'eau >= 70 (240000) | Water-cooled >= 70 (240000) | 9 | [30 empty] | 9 | 4 | 260 | 0.086892 | 4.9596e-05 | -4.3352e-09 | -0.03601 | -2.2819e-05 | 1.9747e-09 | HDD
[63 empty] | 2.44 |  |  |  | Conditionneurs d'air refroidis a l'eau avec economiseur de fluide < 19 (65000) | Water-cooled with fluid economizer < 19 (65000) | 9 | [30 empty] | 9 | 5 | 261 | -0.30639 | -0.0046623 | 1.18e-05 | 0.19328 | 0.0058484 | -1.1816e-05 | CDD
[63 empty] | 2.34 |  |  |  | Conditionneurs d'air refroidis a l'eau avec economiseur de fluide >= 19 (65000) et < 70 (240000) | Water-cooled with fluid economizer >= 19 (65000) and < 70 (240000) | 9 | [30 empty] | 9 | 6 | 262 | -0.29525 | 0.00010947 | -6.3892e-09 | 0.85915 | -3.929e-05 | -1.2916e-09 | HDD
[63 empty] | 2.24 |  |  |  | Conditionneurs d'air refroidis a l'eau avec economiseur de fluide >= 70 (240000) | Water-cooled with fluid economizer >= 70 (240000) | 9 | [30 empty] | 9 | 7 | 263 | -0.029362 | -7.9234e-07 | 2.5895e-10 | 0.0010406 | -1.3599e-07 | 4.0679e-12 | TDD
[63 empty] | 2.39 |  |  |  | Conditionneurs d'air refroidis au glycol < 19 (65000) | Glycol-cooled < 19 (65000) | 9 | [30 empty] | 9 | 8 | 264 | 0.021288 | -1.5326e-06 | 2.3551e-12 | -0.0023726 | 2.5222e-07 | -8.7019e-12 | TDD
[63 empty] | 2.04 |  |  |  | Conditionneurs d'air refroidis au glycol >= 19 (65000) et 70 (240000) | Glycol-cooled >= 19 (65000) and 70 (240000) | 9 | [30 empty] | 9 | 9 | 265 | -0.019775 | -5.4328e-06 | 5.1515e-10 | 0.0021896 | -4.8654e-07 | 2.8631e-11 | TDD
[63 empty] | 1.99 |  |  |  | Conditionneurs d'air refroidis au glycol >= 70 (240000) | Glycol-cooled >= 70 (240000) | 9 | [30 empty] | 9 | 10 | 266 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[63 empty] | 2.34 |  |  |  | Conditionneurs d'air refroidis au glycol avec economiseur de fluide < 19 (65000) | Glycol-cooled with fluid economizer < 19 (65000) | 9 | [30 empty] | 9 | 11 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[63 empty] | 1.99 |  |  |  | Conditionneurs d'air refroidis au glycol avec economiseur de fluide >= 19 (65000) et < 70 (240000) | Glycol-cooled with fluid economizer >= 19 (65000) and < 70 (240000) | 9 | [30 empty] | 9 | 12 | 268 | 0.27613 | 0.00011268 | -1.7357e-09 | 0 | 0 | 0 | HDD
[63 empty] | 1.94 |  |  |  | Conditionneurs d'air refroidis au glycol avec economiseur de fluide >= 70 (240000) | Glycol-cooled with fluid economizer >= 70 (240000) | 9 | [30 empty] | 9 | 13 | 269 | -0.0017502 | 0.00035 | -3.8268e-07 | 5.6037e-05 | -2.1309e-05 | 2.346e-08 | CDD
[63 empty] | 6.06 |  |  |  | Section de traitement de l'air refroidi a l'eau refrigeree < 19 (65000) | Chilled water air handler < 19 (65000) | 9 | [30 empty] | 9 | 14 | 270 | 0.030625 | -0.0012566 | 1.0956e-06 | 0.30855 | -0.0024878 | 3.154e-06 | CDD
[63 empty] | 7.06 |  |  |  | Section de traitement de l'air refroidi a l'eau refrigeree >= 19 (65000) et < 70 (240000) | Chilled water air handler >= 19 (65000) and < 70 (240000) | 9 | [30 empty] | 9 | 15 | 271 | 0.09516 | 0.00029245 | -5.8921e-07 | -0.063929 | -8.2882e-05 | 2.2371e-07 | CDD
[63 empty] | 9.06 |  |  |  | Section de traitement de l'air refroidi a l'eau refrigeree >= 70 (240000) | Chilled water air handler >= 70 (240000) | 9 | [30 empty] | 9 | 16 | 272 | -0.83875 | 7.7788e-05 | -2.9992e-09 | 1.0326 | -0.00011053 | 5.5649e-09 | TDD
[63 empty] | 2.8 |  | Packaged Water Chillers | Packaged Water Chillers | À air avec condenseurs | Air cooled, with condenser, electrically operated | 10 | [30 empty] | 9 | 17 | 273 | 0.018071 | -1.101e-05 | 1.7504e-09 | 0.00095865 | 3.1106e-06 | -8.3545e-10 | HDD
[63 empty] | 3.1 |  |  |  | À air sans condenseurs | Air cooled, without condenser, electrically operated | 10 | [30 empty] | 9 | 18 | 274 | -0.022399 | 9.5836e-05 | -1.3517e-07 | 0.033807 | -3.8507e-05 | 4.8706e-08 | CDD
[63 empty] | 4.2 |  |  |  | À eau, à piston | Water cooled, electrically operated, positive displacement (reciprocating) | 10 | [30 empty] | 9 | 19 | 275 | 0.013676 | -8.4112e-07 | 4.5651e-11 | -0.00079318 | 4.7138e-08 | -2.6005e-12 | HDD
[63 empty] | 4.45 |  |  |  | À eau, rotatif à vis, à volute < 150 Tons | Water cooled, electrically operated, positive displacement (rotary screw and scroll) < 150 Tons | 10 | [30 empty] | 9 | 20 | 276 | -0.00010696 | 4.8422e-06 | -7.1904e-09 | 1.2707e-05 | -3.0506e-07 | 4.5398e-10 | CDD
[63 empty] | 4.9 |  |  |  | À eau, rotatif à vis, à volute >= 150 Tons & < 300 Tons | Water cooled, electrically operated, positive displacement (rotary screw and scroll) >= 150 Tons & < 300 Tons | 10 | [30 empty] | 9 | 21 | 277 | -7.0041e-05 | 5.477e-09 | -4.7242e-13 | 3.0381e-08 | -9.8129e-12 | 8.1489e-16 | HDD
[63 empty] | 5.5 |  |  |  | À eau, rotatif à vis, à volute >= 300 Tons | Water cooled, electrically operated, positive displacement (rotary screw and scroll) >= 300 Tons | 10 | [30 empty] | 9 | 22 | 278 | 3.6148e-06 | -1.4591e-06 | 1.7566e-09 | 3.828e-07 | -2.2453e-09 | 2.6678e-12 | CDD
[63 empty] | 5 |  |  |  | À eau, centrifuge < 150 Tons | Water cooled, electrically operated, positive displacement (centrifugal) < 150 Tons | 10 | [30 empty] | 9 | 23 | 279 | 0.025781 | -3.2528e-06 | 2.6171e-10 | -0.015759 | 2.3481e-06 | -1.8745e-10 | HDD
[63 empty] | 5.55 |  |  |  | À eau, centrifuge >= 150 Tons & < 300 Tons | Water cooled, electrically operated, positive displacement (centrifugal) >= 150 Tons & < 300 Tons | 10 | [30 empty] | 9 | 24 | 280 | -0.010058 | 0.00036861 | -4.5972e-07 | 0.0057885 | -0.00020898 | 2.6425e-07 | CDD
[63 empty] | 6.1 |  |  |  | À eau, centrifuge >= 300 Tons | Water cooled, electrically operated, positive displacement (centrifugal) >= 300 Tons | 10 | [30 empty] | 9 | 25 | 281 | 0.024373 | -6.0634e-06 | 5.7513e-10 | -0.011769 | 3.4819e-06 | -3.2918e-10 | HDD
[63 empty] | 0.6 |  |  |  | Absorption, simple effet, à air | Air cooled absorption single effect | 10 | [30 empty] | 9 | 26 | 282 | -0.013566 | 0.0002666 | -3.3509e-07 | 0.0073503 | -0.00011624 | 1.4841e-07 | CDD
[63 empty] | 0.7 |  |  |  | Absorption, simple effet, à eau | Water cooled absorption single effect | 10 | [30 empty] | 9 | 27 | 283 | -60.7934 | 0.029528 | -2.4649e-06 | 37.6086 | -0.018077 | 1.5063e-06 | HDD
[63 empty] | 1 |  |  |  | Absorption, double effet, indirect | Absorption double effect, indirect-fired | 10 | [30 empty] | 9 | 28 | 284 | -38.6449 | 0.26818 | -0.00041205 | 24.8754 | -0.17048 | 0.00026182 | CDD
[63 empty] | 1 |  |  |  | Absorption, double effet, direct | Absorption double effect, direct-fired | 10 | [30 empty] | 9 | 29 | 285 | 50.1918 | -0.0088014 | 5.1172e-07 | -29.9692 | 0.0052834 | -3.0738e-07 | HDD
[100 empty] | 9 | 30 | 286 | -6.5825 | 0.038662 | -4.1667e-05 | 4.3325 | -0.021244 | 2.1771e-05 | CDD
[100 empty] | 9 | 31 | 287 | 208.862 | -0.045039 | 8.1757e-07 | -207.0608 | 0.04484 | -8.101e-07 | HDD
[100 empty] | 9 | 32 | 288 | -0.0033443 | -0.00011055 | 1.3665e-07 | 0.0043991 | 0.00015674 | -1.8925e-07 | CDD
[100 empty] | 10 | 1 | 289 | 0.018698 | 5.1822e-05 | -3.4793e-09 | -0.0093283 | -2.8162e-05 | 1.8781e-09 | HDD
[100 empty] | 10 | 2 | 290 | 0.013175 | 3.6546e-05 | -2.508e-09 | -0.0040696 | -1.4697e-05 | 1.0176e-09 | HDD
[100 empty] | 10 | 3 | 291 | -0.064908 | 7.9771e-05 | -4.7254e-09 | 0.054479 | -6.9435e-05 | 4.1079e-09 | HDD
[100 empty] | 10 | 4 | 292 | -0.030895 | 3.7756e-05 | -2.2385e-09 | 0.012933 | -1.6381e-05 | 9.7132e-10 | HDD
[100 empty] | 10 | 5 | 293 | -0.21591 | 0.0002962 | -3.9247e-08 | 0.16971 | -0.00017889 | 2.5309e-08 | HDD
[100 empty] | 10 | 6 | 294 | 0.0033391 | 4.953e-06 | -3.3763e-10 | -0.0042937 | -6.4083e-06 | 4.3703e-10 | HDD
[100 empty] | 10 | 7 | 295 | -0.00059655 | -2.8073e-06 | 1.9103e-10 | 9.0632e-06 | 6.8432e-08 | -5.6646e-12 | TDD
[100 empty] | 10 | 8 | 296 | 0.00010666 | -1.3149e-06 | 2.7102e-09 | -9.235e-06 | 1.328e-07 | -2.7098e-10 | HDD
[100 empty] | 10 | 9 | 297 | 0.011517 | -9.8367e-06 | 5.5404e-10 | -0.0016784 | 9.2366e-07 | -6.3233e-11 | TDD
[100 empty] | 10 | 10 | 298 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 10 | 11 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 10 | 12 | 300 | 0.097482 | 5.9785e-05 | -1.3488e-09 | 0 | 0 | 0 | HDD
[100 empty] | 10 | 13 | 301 | 0.0031954 | 2.6758e-05 | -1.5635e-08 | -0.00020554 | -1.6905e-06 | 1.0034e-09 | CDD
[100 empty] | 10 | 14 | 302 | -0.0022293 | -0.00016745 | 1.0939e-07 | -0.030617 | -9.3809e-05 | 2.6443e-07 | CDD
[100 empty] | 10 | 15 | 303 | -1.2504 | -0.00089574 | 2.8205e-06 | 1.439 | 0.0013153 | -3.7112e-06 | CDD
[100 empty] | 10 | 16 | 304 | 64.5308 | -0.11668 | -0.00014937 | -38.1944 | 0.068653 | 9.3392e-05 | CDD
[100 empty] | 10 | 17 | 305 | 0.035067 | -6.6819e-06 | 5.3763e-10 | -0.036417 | 7.0645e-06 | -5.9059e-10 | TDD
[100 empty] | 10 | 18 | 306 | -0.0045302 | 1.8203e-05 | -2.4741e-08 | 0.0070216 | -1.7031e-05 | 2.2988e-08 | CDD
[100 empty] | 10 | 19 | 307 | 0.00029222 | 2.348e-07 | -8.6627e-12 | -2.7372e-05 | -1.1204e-08 | 2.6875e-13 | HDD
[100 empty] | 10 | 20 | 308 | 3.6752e-05 | 1.232e-06 | -1.5013e-09 | -1.3125e-06 | -7.084e-08 | 8.68e-11 | CDD
[100 empty] | 10 | 21 | 309 | -6.47e-06 | -9.4042e-09 | 5.5875e-13 | -2.3825e-08 | 9.6703e-12 | -7.3859e-16 | HDD
[100 empty] | 10 | 22 | 310 | -1.7578e-05 | -3.812e-08 | -1.0952e-11 | 1.247e-07 | -7.219e-10 | 1.0203e-12 | CDD
[100 empty] | 10 | 23 | 311 | 0.0031158 | 2.395e-06 | -1.2939e-10 | -0.0017615 | -1.3039e-06 | 6.853e-11 | HDD
[100 empty] | 10 | 24 | 312 | -0.0012437 | 4.2254e-05 | -4.8982e-08 | 0.0014399 | -2.9558e-05 | 3.6642e-08 | CDD
[100 empty] | 10 | 25 | 313 | 0.00036198 | 2.4508e-06 | -1.6923e-10 | 0.00012884 | -1.0496e-06 | 7.6372e-11 | HDD
[100 empty] | 10 | 26 | 314 | 0.00047395 | 9.2598e-06 | -1.7556e-09 | -9.1031e-05 | -3.0233e-06 | -6.8678e-10 | CDD
[100 empty] | 10 | 27 | 315 | -131.7341 | 0.049934 | -4.1934e-06 | 81.2024 | -0.030543 | 2.5646e-06 | HDD
[100 empty] | 10 | 28 | 316 | 324.8617 | -2.0721 | 0.0027918 | -199.1207 | 1.2739 | -0.0017163 | CDD
[100 empty] | 10 | 29 | 317 | 462.807 | -0.087229 | -4.0835e-07 | -289.1642 | 0.05471 | 2.3989e-07 | HDD
[100 empty] | 10 | 30 | 318 | -123.4907 | 0.65018 | -0.0007212 | 77.6432 | -0.40554 | 0.00044988 | CDD
[100 empty] | 10 | 31 | 319 | -493.6404 | 0.23256 | -2.3686e-05 | 308.3001 | -0.14504 | 1.4779e-05 | HDD
[100 empty] | 10 | 32 | 320 | 171.7621 | -2.2826 | 0.0043346 | -107.0825 | 1.4274 | -0.0027086 | CDD
[100 empty] | 11 | 1 | 321 | -0.080814 | 0.00011447 | -7.7633e-09 | 0.056487 | -7.703e-05 | 5.2347e-09 | HDD
[100 empty] | 11 | 2 | 322 | -0.0226 | 5.8373e-05 | -3.9303e-09 | 0.003936 | -2.1398e-05 | 1.4275e-09 | HDD
[100 empty] | 11 | 3 | 323 | -0.067718 | 0.00010619 | -6.9748e-09 | 0.086988 | -0.00014027 | 9.2181e-09 | HDD
[100 empty] | 11 | 4 | 324 | -0.013721 | 3.1157e-05 | -2.0154e-09 | 0.0039056 | -1.3026e-05 | 8.3406e-10 | HDD
[100 empty] | 11 | 5 | 325 | -2.0503 | 0.00091594 | -7.3271e-08 | 1.4448 | -0.00060639 | 4.9084e-08 | HDD
[100 empty] | 11 | 6 | 326 | -0.0090749 | 1.0349e-05 | -7.2501e-10 | 0.01137 | -1.3236e-05 | 9.2537e-10 | HDD
[100 empty] | 11 | 7 | 327 | 0.0037405 | -6.2315e-06 | 4.2833e-10 | -4.174e-05 | 1.4085e-07 | -1.0537e-11 | HDD
[100 empty] | 11 | 8 | 328 | -0.0007059 | 4.144e-07 | -3.4246e-11 | 0 | 0 | 0 | HDD
[100 empty] | 11 | 9 | 329 | 0.0067215 | -1.0537e-05 | 6.8358e-10 | -0.00040344 | 4.8815e-07 | -2.9679e-11 | HDD
[100 empty] | 11 | 10 | 330 | 3.5279e-05 | 8.9055e-09 | -3.0733e-13 | -5.2411e-07 | -1.2063e-10 | 3.8381e-15 | HDD
[100 empty] | 11 | 11 | 331 | 8.4062e-05 | 2.2532e-08 | -7.9553e-13 | -1.3058e-06 | -3.4007e-10 | 1.1737e-14 | HDD
[100 empty] | 11 | 12 | 332 | 0.14109 | 4.5672e-05 | -2.4644e-10 | 0 | 0 | 0 | HDD
[100 empty] | 11 | 13 | 333 | 0.028175 | -4.6505e-05 | 1.1106e-07 | -0.0026497 | 4.4571e-06 | -1.0339e-08 | CDD
[100 empty] | 11 | 14 | 334 | -0.22154 | -0.0014023 | 1.0614e-06 | -0.18369 | 0.0049891 | -4.405e-06 | CDD
[100 empty] | 11 | 15 | 335 | 0.065479 | 1.6429e-05 | -8.4139e-08 | -0.037584 | -7.6322e-06 | 4.5667e-08 | CDD
[100 empty] | 11 | 16 | 336 | -0.15419 | 1.2475e-05 | -2.1391e-09 | 0.16752 | -6.7707e-06 | 1.964e-09 | TDD
[100 empty] | 11 | 17 | 337 | 0.035067 | -6.6819e-06 | 5.3763e-10 | -0.036417 | 7.0645e-06 | -5.9059e-10 | TDD
[100 empty] | 11 | 18 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 11 | 19 | 339 | 2.2917e-05 | 3.717e-07 | -2.0213e-11 | -1.1279e-05 | -1.9069e-08 | 9.3287e-13 | HDD
[100 empty] | 11 | 20 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 11 | 21 | 341 | -4.5781e-05 | -9.5316e-09 | 2.5826e-13 | 1.1331e-08 | 2.0198e-12 | -1.0458e-16 | HDD
[100 empty] | 11 | 22 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 11 | 23 | 343 | 0.012243 | 3.3394e-06 | -1.1529e-10 | -0.00644 | -1.9822e-06 | 7.467e-11 | HDD
[100 empty] | 11 | 24 | 344 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 11 | 25 | 345 | 0.0082243 | 2.2876e-06 | -7.7931e-11 | -0.0028699 | -9.3946e-07 | 3.5134e-11 | HDD
[100 empty] | 11 | 26 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 11 | 27 | 347 | -125.649 | 0.047823 | -4.0321e-06 | 77.4071 | -0.029232 | 2.4649e-06 | HDD
[100 empty] | 11 | 28 | 348 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 11 | 29 | 349 | -3.454 | 0.0030514 | -2.8267e-07 | 2.1488 | -0.0018784 | 1.7438e-07 | HDD
[100 empty] | 11 | 30 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 11 | 31 | 351 | -194.523 | 0.074739 | -6.3825e-06 | 194.1585 | -0.07429 | 6.3504e-06 | HDD
[100 empty] | 11 | 32 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 12 | 1 | 353 | 0.028087 | 4.9473e-05 | -3.24e-09 | -0.01353 | -2.7219e-05 | 1.7705e-09 | HDD
[100 empty] | 12 | 2 | 354 | 0.019765 | 3.4944e-05 | -2.3651e-09 | -0.0066253 | -1.4078e-05 | 9.6699e-10 | HDD
[100 empty] | 12 | 3 | 355 | -0.059011 | 7.7977e-05 | -4.5364e-09 | 0.049381 | -6.7811e-05 | 3.933e-09 | HDD
[100 empty] | 12 | 4 | 356 | -0.025382 | 3.588e-05 | -2.0394e-09 | 0.0099867 | -1.5356e-05 | 8.6351e-10 | HDD
[100 empty] | 12 | 5 | 357 | -1.7375 | 0.00075447 | -6.0751e-08 | 1.2247 | -0.00050034 | 4.0802e-08 | HDD
[100 empty] | 12 | 6 | 358 | 0.0039846 | 4.8402e-06 | -3.2386e-10 | -0.0051904 | -6.2271e-06 | 4.1459e-10 | HDD
[100 empty] | 12 | 7 | 359 | -0.0026196 | -2.145e-06 | 1.4084e-10 | 0.00016992 | 7.8368e-09 | -1.1052e-12 | TDD
[100 empty] | 12 | 8 | 360 | 0.00013097 | -1.475e-06 | 3.5719e-09 | -1.6737e-05 | 1.9659e-07 | -4.3945e-10 | CDD
[100 empty] | 12 | 9 | 361 | 0.010971 | -9.7278e-06 | 5.4773e-10 | -0.0018186 | 9.9512e-07 | -7.3202e-11 | TDD
[100 empty] | 12 | 10 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 12 | 11 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 12 | 12 | 364 | 0.10618 | 5.704e-05 | -1.1041e-09 | 0 | 0 | 0 | HDD
[100 empty] | 12 | 13 | 365 | 0.0035922 | 2.4384e-05 | -1.1952e-08 | -0.00023447 | -1.5116e-06 | 7.2767e-10 | CDD
[100 empty] | 12 | 14 | 366 | 6.8757e-05 | -0.00019457 | 1.5081e-07 | -0.11342 | 0.00068689 | -1.018e-06 | CDD
[100 empty] | 12 | 15 | 367 | 0.039572 | 2.2095e-05 | -8.2504e-08 | -0.022928 | -9.8243e-06 | 4.344e-08 | CDD
[100 empty] | 12 | 16 | 368 | 0.093181 | -0.00016814 | 9.6937e-09 | -0.11351 | 0.00020488 | -1.1812e-08 | HDD
[100 empty] | 12 | 17 | 369 | 0.0096103 | -1.5295e-06 | 1.2807e-10 | -0.0082864 | 1.6471e-06 | -1.2673e-10 | HDD
[100 empty] | 12 | 18 | 370 | -0.0045165 | 1.7861e-05 | -2.3486e-08 | 0.0072662 | -1.7874e-05 | 2.2953e-08 | CDD
[100 empty] | 12 | 19 | 371 | 0.0003147 | 1.8721e-07 | -3.7709e-12 | -3.0548e-05 | -8.9755e-09 | 4.4965e-14 | TDD
[100 empty] | 12 | 20 | 372 | 0.00027951 | -3.4828e-07 | 7.6166e-10 | -2.6968e-05 | 9.4019e-08 | -1.4901e-10 | CDD
[100 empty] | 12 | 21 | 373 | -4.3014e-06 | -1.0289e-08 | 6.3124e-13 | -6.9098e-09 | 3.755e-12 | -2.8603e-16 | HDD
[100 empty] | 12 | 22 | 374 | -1.0925e-05 | -7.9442e-08 | 5.1725e-11 | 3.5974e-08 | -1.6925e-10 | 1.5399e-13 | CDD
[100 empty] | 12 | 23 | 375 | 0.0012834 | 3.1222e-06 | -1.8928e-10 | -0.00057796 | -1.7797e-06 | 1.0814e-10 | HDD
[100 empty] | 12 | 24 | 376 | 0.0010516 | 1.9954e-05 | -9.5614e-09 | -0.00055298 | -1.0659e-05 | 3.4265e-09 | CDD
[100 empty] | 12 | 25 | 377 | 0.0044453 | 7.8754e-07 | -1.6314e-11 | -0.0023717 | -3.6892e-08 | -1.5915e-11 | HDD
[100 empty] | 12 | 26 | 378 | 0.0018071 | 8.5967e-06 | -6.9991e-09 | -0.00086367 | -2.4519e-06 | 2.0717e-09 | CDD
[100 empty] | 12 | 27 | 379 | -135.4367 | 0.051313 | -4.3081e-06 | 83.5734 | -0.031427 | 2.638e-06 | HDD
[100 empty] | 12 | 28 | 380 | 417.9545 | -2.6034 | 0.0034394 | -256.8856 | 1.6041 | -0.0021194 | CDD
[100 empty] | 12 | 29 | 381 | 4.2249 | -0.0003157 | 4.5773e-08 | -2.6293 | 0.00021199 | -2.9619e-08 | HDD
[100 empty] | 12 | 30 | 382 | 0.79482 | -0.00055899 | 5.8463e-07 | -0.10134 | 6.2328e-05 | -5.8912e-08 | CDD
[100 empty] | 12 | 31 | 383 | -372.3084 | 0.16875 | -1.6704e-05 | 371.6885 | -0.16816 | 1.6655e-05 | HDD
[100 empty] | 12 | 32 | 384 | -319.3149 | 1.818 | -0.0022046 | 319.3603 | -1.8137 | 0.0022007 | CDD
[100 empty] | 13 | 1 | 385 | 1.1498 | -0.00013488 | 5.6129e-09 | -0.60912 | 7.0517e-05 | -2.9708e-09 | HDD
[100 empty] | 13 | 2 | 386 | 0.72954 | -6.9045e-05 | 2.0491e-09 | -0.2563 | 1.8064e-05 | -1.9014e-10 | HDD
[100 empty] | 13 | 3 | 387 | 0.72099 | 2.2851e-05 | -5.5068e-09 | -0.6124 | -2.6681e-05 | 5.2661e-09 | HDD
[100 empty] | 13 | 4 | 388 | 0.32382 | 1.8368e-05 | -3.2381e-09 | -0.13402 | -1.082e-05 | 1.6176e-09 | HDD
[100 empty] | 13 | 5 | 389 | 7.5101 | -0.0023587 | 1.6987e-07 | -4.1917 | 0.0014841 | -1.136e-07 | HDD
[100 empty] | 13 | 6 | 390 | 0.94103 | -0.000127 | 6.0123e-09 | -0.56399 | 7.0847e-05 | -3.1668e-09 | HDD
[100 empty] | 13 | 7 | 391 | -0.077594 | 1.1145e-05 | -5.0717e-10 | 0.0026276 | -4.826e-07 | 2.3647e-11 | HDD
[100 empty] | 13 | 8 | 392 | -0.031547 | 1.4311e-05 | -1.0951e-09 | 0.0040204 | -1.7672e-06 | 1.3421e-10 | TDD
[100 empty] | 13 | 9 | 393 | -0.099371 | 7.158e-07 | 4.7885e-10 | 0.0087364 | -9.0931e-07 | 1.8695e-11 | HDD
[100 empty] | 13 | 10 | 394 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 13 | 11 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 13 | 12 | 396 | 0.82835 | -5.2128e-05 | 9.2128e-09 | 0 | 0 | 0 | HDD
[100 empty] | 13 | 13 | 397 | 0.0016965 | 0.00029082 | -2.54e-07 | -0.00016574 | -1.7707e-05 | 1.5633e-08 | CDD
[100 empty] | 13 | 14 | 398 | -0.0084596 | -0.0011281 | 6.7623e-07 | -0.35874 | 0.0040597 | -6.2593e-06 | CDD
[100 empty] | 13 | 15 | 399 | -0.0064174 | 0.0016683 | -2.7806e-06 | 0.0045453 | -0.00095847 | 1.6e-06 | CDD
[100 empty] | 13 | 16 | 400 | -1.5235 | 0.00029545 | -2.237e-08 | 1.8196 | -0.00034471 | 2.6543e-08 | HDD
[100 empty] | 13 | 17 | 401 | -2.0377 | 0.00093557 | -9.9058e-08 | 3.2383 | -0.0015279 | 1.6998e-07 | TDD
[100 empty] | 13 | 18 | 402 | -0.013299 | 9.7965e-05 | -1.4922e-07 | 0.026678 | -0.00010733 | 1.667e-07 | CDD
[100 empty] | 13 | 19 | 403 | 0.044292 | -7.0232e-06 | 3.5751e-10 | -0.0025386 | 3.7575e-07 | -1.7912e-11 | HDD
[100 empty] | 13 | 20 | 404 | 0.0019544 | -4.8965e-07 | 3.1547e-11 | -4.7888e-05 | 3.3951e-07 | -6.0822e-10 | CDD
[100 empty] | 13 | 21 | 405 | -0.00023065 | 2.0265e-08 | -1.8638e-12 | -2.1993e-07 | 6.267e-11 | -3.7789e-15 | HDD
[100 empty] | 13 | 22 | 406 | 4.0976e-05 | -1.3851e-06 | 1.3313e-09 | -1.8487e-07 | 1.0139e-10 | 1.4438e-12 | CDD
[100 empty] | 13 | 23 | 407 | 0.085348 | -0.0001962 | 2.7929e-07 | -0.048932 | 0.00011657 | -1.6492e-07 | HDD
[100 empty] | 13 | 24 | 408 | 0.01303 | 0.00011496 | -5.1149e-08 | -0.011214 | -2.5667e-05 | -2.806e-08 | CDD
[100 empty] | 13 | 25 | 409 | 0.085805 | -1.6406e-05 | 1.2914e-09 | -0.038083 | 8.084e-06 | -6.3068e-10 | HDD
[100 empty] | 13 | 26 | 410 | -0.0018799 | 0.00013939 | -1.1391e-07 | 0.00029138 | -4.6404e-05 | 2.9808e-08 | CDD
[100 empty] | 13 | 27 | 411 | -2537.1184 | 0.94747 | -7.8911e-05 | 1585.2242 | -0.59176 | 4.9285e-05 | HDD
[100 empty] | 13 | 28 | 412 | 194.5325 | -1.3925 | 0.0020394 | -117.9099 | 0.84897 | -0.0012439 | CDD
[100 empty] | 13 | 29 | 413 | 18.033 | -0.0083039 | 8.669e-07 | -9.0453 | 0.0047148 | -5.1327e-07 | HDD
[100 empty] | 13 | 30 | 414 | -8.7409 | 0.03161 | -1.0093e-05 | 5.6785 | -0.017356 | 3.3081e-06 | CDD
[100 empty] | 13 | 31 | 415 | -159.821 | 0.050056 | -3.2698e-06 | 159.4588 | -0.049652 | 3.2457e-06 | HDD
[100 empty] | 13 | 32 | 416 | -20.4265 | 0.061361 | -2.5514e-06 | 20.1988 | -0.055912 | -2.2424e-06 | CDD
[100 empty] | 14 | 1 | 417 | 6.073 | -0.0015007 | 9.8436e-08 | -2.9036 | 0.00068693 | -4.3981e-08 | HDD
[100 empty] | 14 | 2 | 418 | 4.0939 | -0.00099374 | 6.4498e-08 | -1.3741 | 0.00031265 | -1.9537e-08 | HDD
[100 empty] | 14 | 3 | 419 | 0.9735 | -0.00026411 | 1.8315e-08 | -0.86113 | 0.00023247 | -1.5979e-08 | HDD
[100 empty] | 14 | 4 | 420 | 0.4915 | -0.00013823 | 9.6831e-09 | -0.21642 | 6.0423e-05 | -4.1534e-09 | HDD
[100 empty] | 14 | 5 | 421 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 14 | 6 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 14 | 7 | 423 | -1.2347 | 0.00035462 | -2.5075e-08 | 0.12655 | -3.9915e-05 | 2.9414e-09 | HDD
[100 empty] | 14 | 8 | 424 | -0.0015839 | 3.8598e-05 | -5.8401e-08 | 0.00022473 | -3.9922e-06 | 5.9342e-09 | CDD
[100 empty] | 14 | 9 | 425 | -0.16761 | 4.289e-05 | -2.8691e-09 | 0 | 0 | 0 | TDD
[100 empty] | 14 | 10 | 426 | 0.0027374 | -3.1714e-07 | 1.047e-11 | -4.7459e-05 | 6.0084e-09 | -2.2522e-13 | HDD
[100 empty] | 14 | 11 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 14 | 12 | 428 | 0.3352 | 0.00018326 | -9.0685e-09 | 0 | 0 | 0 | HDD
[100 empty] | 14 | 13 | 429 | -0.016199 | 0.00071906 | -9.0365e-07 | 0.0010321 | -4.4633e-05 | 5.6368e-08 | CDD
[100 empty] | 14 | 14 | 430 | -0.025731 | -0.00072018 | 6.7142e-10 | 2.0721 | -0.016088 | 2.3701e-05 | CDD
[100 empty] | 14 | 15 | 431 | -0.0045883 | 0.00053386 | -8.672e-07 | 0.0050232 | -0.0003266 | 5.278e-07 | CDD
[100 empty] | 14 | 16 | 432 | -4.1679 | 0.001747 | -1.3377e-07 | 3.0973 | -0.0013455 | 1.2911e-07 | TDD
[100 empty] | 14 | 17 | 433 | 0.1691 | -1.5522e-05 | -8.2513e-10 | -0.51167 | 0.00021645 | -1.5573e-08 | TDD
[100 empty] | 14 | 18 | 434 | -0.0011874 | 5.3543e-05 | -7.0733e-08 | 0.00078589 | -3.5438e-05 | 4.6815e-08 | CDD
[100 empty] | 14 | 19 | 435 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 14 | 20 | 436 | 0.081531 | -2.1548e-05 | 1.4627e-09 | -0.0043777 | 1.2192e-06 | -8.6551e-11 | TDD
[100 empty] | 14 | 21 | 437 | -0.0013297 | 2.9566e-07 | -1.9604e-11 | 6.4442e-07 | -1.9629e-10 | 1.5375e-14 | HDD
[100 empty] | 14 | 22 | 438 | -0.0012047 | 2.4692e-07 | -1.529e-11 | 0 | 0 | 0 | TDD
[100 empty] | 14 | 23 | 439 | 0.39141 | -8.5998e-05 | 5.6433e-09 | -0.22095 | 4.8912e-05 | -3.2176e-09 | HDD
[100 empty] | 14 | 24 | 440 | 0.38474 | -8.1174e-05 | 5.1405e-09 | -0.21459 | 4.885e-05 | -3.2978e-09 | TDD
[100 empty] | 14 | 25 | 441 | 0.29902 | -7.1887e-05 | 4.9633e-09 | -0.12206 | 3.0143e-05 | -2.1062e-09 | HDD
[100 empty] | 14 | 26 | 442 | 0.31653 | -7.2626e-05 | 4.7903e-09 | -0.12206 | 3.0143e-05 | -2.1062e-09 | TDD
[100 empty] | 14 | 27 | 443 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 14 | 28 | 444 | 421.7393 | -0.153 | 1.2377e-05 | -261.5936 | 0.095282 | -7.7221e-06 | HDD
[100 empty] | 14 | 29 | 445 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 14 | 30 | 446 | 315.1608 | -0.11154 | 8.7722e-06 | -191.8713 | 0.068223 | -5.3755e-06 | HDD
[100 empty] | 14 | 31 | 447 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 14 | 32 | 448 | 8.0978 | -0.0043077 | 5.0819e-07 | -4.6199 | 0.0035043 | -4.5223e-07 | HDD
[100 empty] | 15 | 1 | 449 | 2.0736 | -0.00045341 | 2.7684e-08 | -1.1725 | 0.00025536 | -1.5543e-08 | HDD
[100 empty] | 15 | 2 | 450 | 1.0621 | -0.00012688 | 1.9333e-09 | -0.33123 | 2.4706e-06 | 3.6434e-09 | HDD
[100 empty] | 15 | 3 | 451 | 0.35274 | -9.2501e-05 | 6.3815e-09 | -0.32502 | 8.1894e-05 | -5.4379e-09 | HDD
[100 empty] | 15 | 4 | 452 | 0.19085 | -4.2745e-05 | 2.817e-09 | -0.08581 | 1.9331e-05 | -1.2831e-09 | HDD
[100 empty] | 15 | 5 | 453 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 15 | 6 | 454 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 15 | 7 | 455 | -0.15788 | 3.4056e-05 | -2.0798e-09 | -0.0033804 | 4.8863e-07 | 1.164e-12 | TDD
[100 empty] | 15 | 8 | 456 | 0.0015137 | 3.5639e-05 | -6.0322e-08 | -0.00021026 | -3.2395e-06 | 5.6502e-09 | CDD
[100 empty] | 15 | 9 | 457 | -0.065876 | 1.2672e-05 | -7.3204e-10 | -0.00068598 | 7.0356e-07 | -6.7574e-11 | TDD
[100 empty] | 15 | 10 | 458 | 0.00090733 | -9.233e-08 | 5.4768e-12 | -1.2021e-05 | 1.0012e-09 | -5.5984e-14 | HDD
[100 empty] | 15 | 11 | 459 | 0.0005464 | -7.9054e-08 | 4.9478e-12 | -7.6672e-06 | 1.0034e-09 | -5.9597e-14 | HDD
[100 empty] | 15 | 12 | 460 | 0.40782 | 0.00010275 | -4.1189e-09 | 0 | 0 | 0 | HDD
[100 empty] | 15 | 13 | 461 | -0.0042353 | 0.00030609 | -3.4805e-07 | 0.0002635 | -1.9122e-05 | 2.1867e-08 | CDD
[100 empty] | 15 | 14 | 462 | 0.019007 | -0.0010989 | 1.0789e-06 | -0.64091 | 0.0025741 | -2.9562e-06 | CDD
[100 empty] | 15 | 15 | 463 | -0.0076096 | 0.00027515 | -4.789e-07 | 0.0052356 | -0.00016455 | 2.842e-07 | CDD
[100 empty] | 15 | 16 | 464 | -5.4394 | 0.002454 | -1.8726e-07 | 20.3996 | -0.0094294 | 8.3315e-07 | TDD
[100 empty] | 15 | 17 | 465 | -0.052282 | 1.6685e-05 | -1.9688e-09 | -0.098662 | 7.6553e-05 | -5.3758e-09 | HDD
[100 empty] | 15 | 18 | 466 | 0.013563 | 0.00049804 | -7.95e-07 | -0.011644 | -0.00023185 | 3.8205e-07 | CDD
[100 empty] | 15 | 19 | 467 | 0.014494 | 9.114e-07 | -1.7379e-10 | 0.0022424 | -5.8494e-07 | 3.8818e-11 | HDD
[100 empty] | 15 | 20 | 468 | 0.002311 | -1.5426e-05 | 2.3874e-08 | -0.00018502 | 1.3911e-06 | -2.1538e-09 | CDD
[100 empty] | 15 | 21 | 469 | -0.0011761 | 2.5859e-07 | -1.7742e-11 | 3.9226e-06 | -1.1524e-09 | 8.2344e-14 | HDD
[100 empty] | 15 | 22 | 470 | 3.691e-05 | -1.5018e-06 | 2.0311e-09 | -9.5817e-08 | 3.2561e-10 | -3.339e-13 | CDD
[100 empty] | 15 | 23 | 471 | 0.19118 | -3.3646e-05 | 2.3782e-09 | -0.095452 | 1.6048e-05 | -1.163e-09 | HDD
[100 empty] | 15 | 24 | 472 | -0.0064483 | 0.0003547 | -5.0527e-07 | 0.0038482 | -0.00021101 | 3.0527e-07 | CDD
[100 empty] | 15 | 25 | 473 | 0.14191 | -1.9228e-05 | 1.1147e-09 | -0.048684 | 5.6836e-06 | -3.0473e-10 | HDD
[100 empty] | 15 | 26 | 474 | 0.013351 | 3.3344e-05 | -3.1385e-08 | -0.0080411 | 9.8212e-06 | -2.0118e-08 | CDD
[100 empty] | 15 | 27 | 475 | -63.0409 | 0.021423 | -1.5604e-06 | 39.3111 | -0.013108 | 9.5048e-07 | HDD
[100 empty] | 15 | 28 | 476 | 5.7475 | -0.064616 | 0.00011956 | -3.4423 | 0.044337 | -8.073e-05 | CDD
[100 empty] | 15 | 29 | 477 | -38.7267 | 0.013495 | -1.0037e-06 | 24.3778 | -0.0082299 | 6.0702e-07 | HDD
[100 empty] | 15 | 30 | 478 | 1.9759 | -0.013065 | 2.9067e-05 | -1.1963 | 0.012704 | -2.4978e-05 | CDD
[100 empty] | 15 | 31 | 479 | 7.866 | -0.00236 | 1.7826e-07 | -5.5504 | 0.0019523 | -1.5181e-07 | HDD
[100 empty] | 15 | 32 | 480 | 6.7652 | -0.011304 | -1.0921e-05 | -6.8793 | 0.018754 | 7.273e-07 | CDD
[100 empty] | 16 | 1 | 481 | 2.0736 | -0.00045341 | 2.7684e-08 | -1.1725 | 0.00025536 | -1.5543e-08 | HDD
[100 empty] | 16 | 2 | 482 | 1.0621 | -0.00012688 | 1.9333e-09 | -0.33123 | 2.4706e-06 | 3.6434e-09 | HDD
[100 empty] | 16 | 3 | 483 | 0.35274 | -9.2501e-05 | 6.3815e-09 | -0.32502 | 8.1894e-05 | -5.4379e-09 | HDD
[100 empty] | 16 | 4 | 484 | 0.19085 | -4.2745e-05 | 2.817e-09 | -0.08581 | 1.9331e-05 | -1.2831e-09 | HDD
[100 empty] | 16 | 5 | 485 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 16 | 6 | 486 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 16 | 7 | 487 | -0.15788 | 3.4056e-05 | -2.0798e-09 | -0.0033804 | 4.8863e-07 | 1.164e-12 | TDD
[100 empty] | 16 | 8 | 488 | 0.0015137 | 3.5639e-05 | -6.0322e-08 | -0.00021026 | -3.2395e-06 | 5.6502e-09 | CDD
[100 empty] | 16 | 9 | 489 | -0.065876 | 1.2672e-05 | -7.3204e-10 | -0.00068598 | 7.0356e-07 | -6.7574e-11 | TDD
[100 empty] | 16 | 10 | 490 | 0.00090733 | -9.233e-08 | 5.4768e-12 | -1.2021e-05 | 1.0012e-09 | -5.5984e-14 | HDD
[100 empty] | 16 | 11 | 491 | 0.0005464 | -7.9054e-08 | 4.9478e-12 | -7.6672e-06 | 1.0034e-09 | -5.9597e-14 | HDD
[100 empty] | 16 | 12 | 492 | 0.40782 | 0.00010275 | -4.1189e-09 | 0 | 0 | 0 | HDD
[100 empty] | 16 | 13 | 493 | -0.0042353 | 0.00030609 | -3.4805e-07 | 0.0002635 | -1.9122e-05 | 2.1867e-08 | CDD
[100 empty] | 16 | 14 | 494 | 0.019007 | -0.0010989 | 1.0789e-06 | -0.64091 | 0.0025741 | -2.9562e-06 | CDD
[100 empty] | 16 | 15 | 495 | -0.0076096 | 0.00027515 | -4.789e-07 | 0.0052356 | -0.00016455 | 2.842e-07 | CDD
[100 empty] | 16 | 16 | 496 | -5.4394 | 0.002454 | -1.8726e-07 | 20.3996 | -0.0094294 | 8.3315e-07 | TDD
[100 empty] | 16 | 17 | 497 | -0.052282 | 1.6685e-05 | -1.9688e-09 | -0.098662 | 7.6553e-05 | -5.3758e-09 | HDD
[100 empty] | 16 | 18 | 498 | 0.013563 | 0.00049804 | -7.95e-07 | -0.011644 | -0.00023185 | 3.8205e-07 | CDD
[100 empty] | 16 | 19 | 499 | 0.014494 | 9.114e-07 | -1.7379e-10 | 0.0022424 | -5.8494e-07 | 3.8818e-11 | HDD
[100 empty] | 16 | 20 | 500 | 0.002311 | -1.5426e-05 | 2.3874e-08 | -0.00018502 | 1.3911e-06 | -2.1538e-09 | CDD
[100 empty] | 16 | 21 | 501 | -0.0011761 | 2.5859e-07 | -1.7742e-11 | 3.9226e-06 | -1.1524e-09 | 8.2344e-14 | HDD
[100 empty] | 16 | 22 | 502 | 3.691e-05 | -1.5018e-06 | 2.0311e-09 | -9.5817e-08 | 3.2561e-10 | -3.339e-13 | CDD
[100 empty] | 16 | 23 | 503 | 0.19118 | -3.3646e-05 | 2.3782e-09 | -0.095452 | 1.6048e-05 | -1.163e-09 | HDD
[100 empty] | 16 | 24 | 504 | -0.0064483 | 0.0003547 | -5.0527e-07 | 0.0038482 | -0.00021101 | 3.0527e-07 | CDD
[100 empty] | 16 | 25 | 505 | 0.14191 | -1.9228e-05 | 1.1147e-09 | -0.048684 | 5.6836e-06 | -3.0473e-10 | HDD
[100 empty] | 16 | 26 | 506 | 0.013351 | 3.3344e-05 | -3.1385e-08 | -0.0080411 | 9.8212e-06 | -2.0118e-08 | CDD
[100 empty] | 16 | 27 | 507 | -63.0409 | 0.021423 | -1.5604e-06 | 39.3111 | -0.013108 | 9.5048e-07 | HDD
[100 empty] | 16 | 28 | 508 | 5.7475 | -0.064616 | 0.00011956 | -3.4423 | 0.044337 | -8.073e-05 | CDD
[100 empty] | 16 | 29 | 509 | -38.7267 | 0.013495 | -1.0037e-06 | 24.3778 | -0.0082299 | 6.0702e-07 | HDD
[100 empty] | 16 | 30 | 510 | 1.9759 | -0.013065 | 2.9067e-05 | -1.1963 | 0.012704 | -2.4978e-05 | CDD
[100 empty] | 16 | 31 | 511 | 7.866 | -0.00236 | 1.7826e-07 | -5.5504 | 0.0019523 | -1.5181e-07 | HDD
[100 empty] | 16 | 32 | 512 | 6.7652 | -0.011304 | -1.0921e-05 | -6.8793 | 0.018754 | 7.273e-07 | CDD
[100 empty] | 17 | 1 | 513 | 4.5819 | -0.00092777 | 5.5692e-08 | -2.0955 | 0.000386 | -2.2043e-08 | HDD
[100 empty] | 17 | 2 | 514 | 2.9956 | -0.00058656 | 3.4399e-08 | -0.91124 | 0.00015029 | -7.8303e-09 | HDD
[100 empty] | 17 | 3 | 515 | 0.56731 | -0.00013368 | 9.0056e-09 | -0.47763 | 0.00011081 | -7.3903e-09 | HDD
[100 empty] | 17 | 4 | 516 | 0.2438 | -5.4404e-05 | 3.4392e-09 | -0.092778 | 1.8657e-05 | -1.0369e-09 | HDD
[100 empty] | 17 | 5 | 517 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 17 | 6 | 518 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 17 | 7 | 519 | -0.97988 | 0.00024556 | -1.599e-08 | 0.09777 | -2.71e-05 | 1.8082e-09 | HDD
[100 empty] | 17 | 8 | 520 | -2.2333e-05 | 5.7519e-06 | -8.2284e-09 | -4.5868e-05 | -5.083e-07 | 7.4126e-10 | CDD
[100 empty] | 17 | 9 | 521 | -0.098508 | 1.9388e-05 | -1.069e-09 | -0.013714 | 6.5068e-06 | -6.4458e-10 | TDD
[100 empty] | 17 | 10 | 522 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 17 | 11 | 523 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 17 | 12 | 524 | -0.75727 | 0.00033583 | -1.6375e-08 | 0 | 0 | 0 | HDD
[100 empty] | 17 | 13 | 525 | 0.0075164 | 0.0023071 | -3.1083e-06 | -0.0028075 | -0.00018979 | 2.5497e-07 | CDD
[100 empty] | 17 | 14 | 526 | 0.033857 | -0.0021845 | 2.3311e-06 | -0.24962 | -0.00027241 | 1.9425e-06 | CDD
[100 empty] | 17 | 15 | 527 | 0.00050294 | -8.6182e-06 | 1.6196e-08 | -0.00071022 | 1.2036e-05 | -2.3014e-08 | CDD
[100 empty] | 17 | 16 | 528 | -2.155 | 0.0028249 | -2.4731e-07 | -11.9367 | -0.0043318 | 6.4978e-07 | TDD
[100 empty] | 17 | 17 | 529 | 0.25466 | -3.2025e-05 | 9.3715e-12 | -0.57442 | 0.00023333 | -1.5885e-08 | HDD
[100 empty] | 17 | 18 | 530 | 0.029214 | -1.029e-05 | 1.0799e-09 | -1.209e-05 | -8.1272e-07 | 2.7248e-11 | CDD
[100 empty] | 17 | 19 | 531 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 17 | 20 | 532 | 0.0046291 | -8.8327e-07 | 4.9595e-11 | -0.00024975 | 5.1807e-08 | -3.186e-12 | TDD
[100 empty] | 17 | 21 | 533 | 0 | 0 | 0 | 0 | 0 | 0 | TDD
[100 empty] | 17 | 22 | 534 | -0.0061632 | 1.4126e-06 | -8.5881e-11 | 1.2405e-06 | -6.5771e-10 | 5.0008e-14 | TDD
[100 empty] | 17 | 23 | 535 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 17 | 24 | 536 | 1.3262 | -0.00028111 | 1.6741e-08 | -0.63513 | 0.00012438 | -6.9897e-09 | HDD
[100 empty] | 17 | 25 | 537 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 17 | 26 | 538 | 0.82236 | -0.00011366 | 5.6771e-09 | -0.27208 | 3.3029e-05 | -1.5456e-09 | HDD
[100 empty] | 17 | 27 | 539 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 17 | 28 | 540 | 0.4858 | -0.00011668 | 7.4318e-09 | 2.486 | -0.00058834 | 3.7064e-08 | HDD
[100 empty] | 17 | 29 | 541 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 17 | 30 | 542 | -255.6096 | 0.07417 | -4.2291e-06 | 158.3893 | -0.045839 | 2.6204e-06 | HDD
[100 empty] | 17 | 31 | 543 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 17 | 32 | 544 | -125.7639 | 0.040466 | -2.7526e-06 | 122.0892 | -0.038921 | 2.642e-06 | HDD
[100 empty] | 18 | 1 | 545 | 1.1716 | -0.00025959 | 1.7811e-08 | -0.67381 | 0.00015203 | -1.0489e-08 | HDD
[100 empty] | 18 | 2 | 546 | 0.99496 | -0.00024184 | 1.7136e-08 | -0.45748 | 0.00011692 | -8.4499e-09 | HDD
[100 empty] | 18 | 3 | 547 | 0.92816 | -0.00019264 | 1.2412e-08 | -0.8421 | 0.00017473 | -1.1154e-08 | HDD
[100 empty] | 18 | 4 | 548 | 0.36356 | -6.4093e-05 | 3.6896e-09 | -0.16096 | 2.7359e-05 | -1.5017e-09 | HDD
[100 empty] | 18 | 5 | 549 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 18 | 6 | 550 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 18 | 7 | 551 | -0.10161 | 2.3481e-05 | -1.7823e-09 | 0.0030316 | -1.1239e-06 | 1.2323e-10 | HDD
[100 empty] | 18 | 8 | 552 | 0.025923 | -0.00014816 | 2.1506e-07 | -0.0043627 | 2.7086e-05 | -3.6514e-08 | CDD
[100 empty] | 18 | 9 | 553 | -0.20685 | 4.83e-05 | -3.4272e-09 | 0.048829 | -1.7339e-05 | 1.4957e-09 | TDD
[100 empty] | 18 | 10 | 554 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 18 | 11 | 555 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 18 | 12 | 556 | 0.065172 | 4.9277e-05 | -9.7412e-10 | 0 | 0 | 0 | HDD
[100 empty] | 18 | 13 | 557 | 0.023155 | 0.0011693 | -1.549e-06 | -0.0019957 | -9.4584e-05 | 1.2452e-07 | CDD
[100 empty] | 18 | 14 | 558 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 18 | 15 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 18 | 16 | 560 | -8.3317 | 0.0056106 | -3.2028e-07 | 22.7878 | -0.022203 | 1.401e-06 | TDD
[100 empty] | 18 | 17 | 561 | 0.35345 | -4.8414e-05 | 6.9036e-10 | -0.50656 | 0.00019626 | -1.1562e-08 | HDD
[100 empty] | 18 | 18 | 562 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 18 | 19 | 563 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 18 | 20 | 564 | 0.0070345 | -1.3138e-06 | 1.0188e-10 | -0.00021232 | 9.4828e-09 | -8.7563e-13 | TDD
[100 empty] | 18 | 21 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | TDD
[100 empty] | 18 | 22 | 566 | -0.037688 | 6.2706e-06 | -4.2632e-10 | 0.00014115 | -2.6415e-08 | 1.7418e-12 | HDD
[100 empty] | 18 | 23 | 567 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 18 | 24 | 568 | 4.2021 | -0.00053075 | 3.8976e-08 | -1.8073 | 0.0001936 | -1.4994e-08 | HDD
[100 empty] | 18 | 25 | 569 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 18 | 26 | 570 | 3.0789 | -0.00043606 | 3.2153e-08 | -0.9669 | 0.00013351 | -1.0201e-08 | HDD
[100 empty] | 18 | 27 | 571 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 18 | 28 | 572 | 1533.8737 | -0.39211 | 2.7097e-05 | -940.7313 | 0.2405 | -1.6623e-05 | HDD
[100 empty] | 18 | 29 | 573 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 18 | 30 | 574 | 3243.1783 | -1.5458 | 0.00015897 | -2022.9625 | 0.9648 | -9.9243e-05 | HDD
[100 empty] | 18 | 31 | 575 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 18 | 32 | 576 | -763.1838 | 0.18559 | -1.2352e-05 | 778.4254 | -0.18849 | 1.2551e-05 | HDD
[100 empty] | 19 | 1 | 577 | 2.2349 | -0.00037193 | 1.7662e-08 | -1.0721 | 0.00015659 | -6.3125e-09 | HDD
[100 empty] | 19 | 2 | 578 | 1.6882 | -0.00028454 | 1.3877e-08 | -0.61752 | 9.0888e-05 | -3.836e-09 | HDD
[100 empty] | 19 | 3 | 579 | 1.7697 | -0.0002034 | 6.8954e-09 | -1.5902 | 0.00021479 | -9.7989e-09 | TDD
[100 empty] | 19 | 4 | 580 | 0.87778 | -0.00010895 | 4.1518e-09 | -0.4056 | 6.1071e-05 | -3.0947e-09 | TDD
[100 empty] | 19 | 5 | 581 | 15.8708 | -0.0046043 | 3.0692e-07 | -10.3751 | 0.0030191 | -2.0085e-07 | HDD
[100 empty] | 19 | 6 | 582 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 19 | 7 | 583 | -0.14497 | 3.6197e-05 | -2.3536e-09 | 0.004672 | -1.4201e-06 | 1.0146e-10 | HDD
[100 empty] | 19 | 8 | 584 | -0.011888 | 0.00020841 | -2.9579e-07 | 0.0012286 | -2.179e-05 | 3.0853e-08 | CDD
[100 empty] | 19 | 9 | 585 | -0.16765 | 2.4053e-05 | -1.0156e-09 | 0.011575 | -2.7828e-06 | 1.7021e-10 | TDD
[100 empty] | 19 | 10 | 586 | 0.0017086 | -1.997e-07 | 8.5291e-12 | -2.557e-05 | 2.942e-09 | -1.2605e-13 | HDD
[100 empty] | 19 | 11 | 587 | 0.00048424 | -1.1768e-08 | -1.8458e-12 | -7.5258e-06 | 1.2475e-10 | 3.4056e-14 | HDD
[100 empty] | 19 | 12 | 588 | 0.82064 | 2.8969e-05 | 1.4349e-09 | 0 | 0 | 0 | HDD
[100 empty] | 19 | 13 | 589 | -0.0032481 | 0.00014354 | -4.4045e-08 | 0.00024929 | -9.6443e-06 | 3.6576e-09 | CDD
[100 empty] | 19 | 14 | 590 | 0.013291 | -0.00043182 | -3.2464e-07 | -0.12564 | -0.00093933 | 1.8556e-06 | CDD
[100 empty] | 19 | 15 | 591 | -0.0017928 | 5.9175e-05 | -6.4336e-08 | 0.0010231 | -3.377e-05 | 3.6716e-08 | CDD
[100 empty] | 19 | 16 | 592 | -1.6642 | 0.001117 | -1.3991e-08 | 6.8798 | -0.0047675 | 4.8115e-08 | HDD
[100 empty] | 19 | 17 | 593 | -0.046019 | 1.1092e-06 | 5.328e-09 | 0 | 0 | 0 | TDD
[100 empty] | 19 | 18 | 594 | -0.00026596 | 5.774e-06 | -4.2961e-09 | 0.00017603 | -3.8216e-06 | 2.8434e-09 | CDD
[100 empty] | 19 | 19 | 595 | 0.049143 | -1.1402e-05 | 7.5925e-10 | -0.0023373 | 5.034e-07 | -3.1975e-11 | HDD
[100 empty] | 19 | 20 | 596 | 0.0043794 | 6.3562e-05 | -9.4928e-08 | -0.00031381 | -2.4377e-06 | 3.2973e-09 | CDD
[100 empty] | 19 | 21 | 597 | -0.00054018 | 1.263e-08 | 1.9582e-12 | -2.3799e-07 | 1.0533e-10 | -7.4908e-15 | HDD
[100 empty] | 19 | 22 | 598 | -0.00015913 | -1.5245e-06 | 1.8525e-09 | -3.3242e-08 | 1.3408e-09 | -1.744e-12 | CDD
[100 empty] | 19 | 23 | 599 | 0.20607 | -2.0091e-05 | 6.9555e-10 | -0.12467 | 1.5077e-05 | -7.0775e-10 | HDD
[100 empty] | 19 | 24 | 600 | 0.057589 | 0.00038501 | -4.8205e-07 | -0.034687 | -0.00019847 | 2.5195e-07 | CDD
[100 empty] | 19 | 25 | 601 | 0.080372 | 8.6162e-06 | -1.3744e-09 | -0.020088 | -6.9644e-06 | 8.2538e-10 | HDD
[100 empty] | 19 | 26 | 602 | -0.001409 | 0.00053879 | -7.1829e-07 | 0.0074644 | -0.00024908 | 3.3569e-07 | CDD
[100 empty] | 19 | 27 | 603 | -27.6402 | 0.0082301 | -4.6367e-07 | 20.504 | -0.0058819 | 3.3019e-07 | HDD
[100 empty] | 19 | 28 | 604 | 17.4758 | -0.12069 | 0.00017876 | -11.8623 | 0.086606 | -0.00012802 | CDD
[100 empty] | 19 | 29 | 605 | -25.632 | 0.009394 | -7.3303e-07 | 19.0041 | -0.0066207 | 5.0875e-07 | HDD
[100 empty] | 19 | 30 | 606 | -507.9626 | 1.8306 | -0.00095794 | 316.8134 | -1.1393 | 0.00059573 | CDD
[100 empty] | 19 | 31 | 607 | 76.7512 | -0.025667 | 1.9025e-06 | -73.8448 | 0.025094 | -1.8672e-06 | HDD
[100 empty] | 19 | 32 | 608 | 0.10836 | 0.0015393 | -2.0125e-06 | -0.064337 | -0.0010104 | 1.3372e-06 | CDD
[100 empty] | 20 | 1 | 609 | 0.40948 | 6.1399e-05 | -8.9225e-09 | -0.16515 | -5.0418e-05 | 5.9823e-09 | HDD
[100 empty] | 20 | 2 | 610 | 0.24943 | 6.3582e-05 | -8.1043e-09 | -0.053611 | -4.2316e-05 | 4.5128e-09 | HDD
[100 empty] | 20 | 3 | 611 | 0.1538 | 0.00012821 | -1.1721e-08 | -0.18568 | -0.00010059 | 9.6072e-09 | TDD
[100 empty] | 20 | 4 | 612 | 0.074027 | 6.0325e-05 | -5.5365e-09 | -0.044247 | -2.3632e-05 | 2.2666e-09 | TDD
[100 empty] | 20 | 5 | 613 | 5.6067 | -0.0011897 | 5.8692e-08 | -3.4189 | 0.00073965 | -3.6126e-08 | HDD
[100 empty] | 20 | 6 | 614 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 20 | 7 | 615 | -0.037328 | 5.4249e-06 | -2.1397e-10 | 0.0013851 | -3.5427e-07 | 2.2287e-11 | HDD
[100 empty] | 20 | 8 | 616 | 0.041942 | -2.7284e-06 | -1.0534e-10 | -0.003988 | 1.661e-07 | 1.9045e-11 | HDD
[100 empty] | 20 | 9 | 617 | -0.017002 | -7.5537e-06 | 7.6104e-10 | 0.001794 | -3.6855e-07 | 1.7355e-11 | TDD
[100 empty] | 20 | 10 | 618 | 0.00031733 | 4.2031e-08 | -2.701e-12 | -4.1726e-06 | -6.1376e-10 | 3.9727e-14 | HDD
[100 empty] | 20 | 11 | 619 | 0.0003197 | -3.0175e-08 | 2.1712e-12 | -4.8282e-06 | 5.0345e-10 | -3.7063e-14 | HDD
[100 empty] | 20 | 12 | 620 | 0.26449 | 0.00014525 | -5.8442e-09 | 0 | 0 | 0 | HDD
[100 empty] | 20 | 13 | 621 | 0.00021715 | 0.00022176 | -2.2998e-07 | -3.3437e-05 | -1.376e-05 | 1.4329e-08 | CDD
[100 empty] | 20 | 14 | 622 | -0.011 | -0.00074427 | 4.7968e-07 | -0.026061 | -0.00064733 | 7.6384e-07 | CDD
[100 empty] | 20 | 15 | 623 | -0.0017928 | 5.9175e-05 | -6.4336e-08 | 0.0010231 | -3.377e-05 | 3.6716e-08 | CDD
[100 empty] | 20 | 16 | 624 | -0.39828 | 0.00042585 | 6.1368e-09 | 1.8239 | -0.0019048 | -2.5576e-08 | HDD
[100 empty] | 20 | 17 | 625 | -0.046019 | 1.1092e-06 | 5.328e-09 | 0 | 0 | 0 | TDD
[100 empty] | 20 | 18 | 626 | -0.012525 | -3.3042e-05 | 6.6233e-08 | 0.01615 | 9.9959e-05 | -1.6918e-07 | CDD
[100 empty] | 20 | 19 | 627 | 0.024026 | -4.8254e-06 | 3.5722e-10 | -0.0028966 | 8.9461e-07 | -6.9907e-11 | HDD
[100 empty] | 20 | 20 | 628 | -0.0001048 | 2.5328e-06 | -3.3212e-09 | 1.0522e-05 | -1.4019e-07 | 1.7068e-10 | CDD
[100 empty] | 20 | 21 | 629 | -0.00017042 | -9.7853e-09 | 7.2421e-13 | 7.0546e-08 | 8.1529e-10 | -1.2928e-12 | HDD
[100 empty] | 20 | 22 | 630 | 2.1428e-05 | -9.0007e-07 | 1.0304e-09 | -1.0209e-07 | 7.3748e-10 | -6.9465e-13 | CDD
[100 empty] | 20 | 23 | 631 | 0.049465 | 2.1427e-06 | -2.1149e-10 | -0.02695 | -1.4375e-06 | 1.4904e-10 | HDD
[100 empty] | 20 | 24 | 632 | 0.0025255 | 0.00012528 | -1.2549e-07 | -0.0026739 | -5.7283e-05 | 4.9671e-08 | CDD
[100 empty] | 20 | 25 | 633 | 0.023141 | 6.2595e-06 | -5.8003e-10 | -0.0062757 | -3.3477e-06 | 3.1489e-10 | HDD
[100 empty] | 20 | 26 | 634 | -0.01343 | 0.00017661 | -2.0941e-07 | 0.0074671 | -8.1393e-05 | 9.6813e-08 | CDD
[100 empty] | 20 | 27 | 635 | -4.3375 | 0.0020855 | -1.8208e-07 | 2.9699 | -0.0011385 | 9.7509e-08 | HDD
[100 empty] | 20 | 28 | 636 | 612.8053 | -8.9308 | 0.01734 | -384.2181 | 5.6096 | -0.010892 | CDD
[100 empty] | 20 | 29 | 637 | -10.3458 | 0.0047508 | -4.4212e-07 | 6.4205 | -0.0026488 | 2.4333e-07 | HDD
[100 empty] | 20 | 30 | 638 | -43.0081 | 0.33109 | -0.00049847 | 27.0141 | -0.20358 | 0.0003068 | CDD
[100 empty] | 20 | 31 | 639 | 0.74139 | 0.00022446 | -3.0221e-08 | 0.1982 | -0.00020177 | 2.8318e-08 | HDD
[100 empty] | 20 | 32 | 640 | 0.0012599 | -8.1488e-05 | 8.2968e-08 | -0.00045128 | 9.2509e-05 | -1.0179e-07 | CDD
[100 empty] | 21 | 1 | 641 | 0.40948 | 6.1399e-05 | -8.9225e-09 | -0.16515 | -5.0418e-05 | 5.9823e-09 | HDD
[100 empty] | 21 | 2 | 642 | 0.24943 | 6.3582e-05 | -8.1043e-09 | -0.053611 | -4.2316e-05 | 4.5128e-09 | HDD
[100 empty] | 21 | 3 | 643 | 0.1538 | 0.00012821 | -1.1721e-08 | -0.18568 | -0.00010059 | 9.6072e-09 | TDD
[100 empty] | 21 | 4 | 644 | 0.074027 | 6.0325e-05 | -5.5365e-09 | -0.044247 | -2.3632e-05 | 2.2666e-09 | TDD
[100 empty] | 21 | 5 | 645 | 5.6067 | -0.0011897 | 5.8692e-08 | -3.4189 | 0.00073965 | -3.6126e-08 | HDD
[100 empty] | 21 | 6 | 646 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 21 | 7 | 647 | -0.037328 | 5.4249e-06 | -2.1397e-10 | 0.0013851 | -3.5427e-07 | 2.2287e-11 | HDD
[100 empty] | 21 | 8 | 648 | 0.041942 | -2.7284e-06 | -1.0534e-10 | -0.003988 | 1.661e-07 | 1.9045e-11 | HDD
[100 empty] | 21 | 9 | 649 | -0.017002 | -7.5537e-06 | 7.6104e-10 | 0.001794 | -3.6855e-07 | 1.7355e-11 | TDD
[100 empty] | 21 | 10 | 650 | 0.00031733 | 4.2031e-08 | -2.701e-12 | -4.1726e-06 | -6.1376e-10 | 3.9727e-14 | HDD
[100 empty] | 21 | 11 | 651 | 0.0003197 | -3.0175e-08 | 2.1712e-12 | -4.8282e-06 | 5.0345e-10 | -3.7063e-14 | HDD
[100 empty] | 21 | 12 | 652 | 0.26449 | 0.00014525 | -5.8442e-09 | 0 | 0 | 0 | HDD
[100 empty] | 21 | 13 | 653 | 0.00021715 | 0.00022176 | -2.2998e-07 | -3.3437e-05 | -1.376e-05 | 1.4329e-08 | CDD
[100 empty] | 21 | 14 | 654 | -0.011 | -0.00074427 | 4.7968e-07 | -0.026061 | -0.00064733 | 7.6384e-07 | CDD
[100 empty] | 21 | 15 | 655 | -0.0017928 | 5.9175e-05 | -6.4336e-08 | 0.0010231 | -3.377e-05 | 3.6716e-08 | CDD
[100 empty] | 21 | 16 | 656 | -0.39828 | 0.00042585 | 6.1368e-09 | 1.8239 | -0.0019048 | -2.5576e-08 | HDD
[100 empty] | 21 | 17 | 657 | -0.046019 | 1.1092e-06 | 5.328e-09 | 0 | 0 | 0 | TDD
[100 empty] | 21 | 18 | 658 | -0.012525 | -3.3042e-05 | 6.6233e-08 | 0.01615 | 9.9959e-05 | -1.6918e-07 | CDD
[100 empty] | 21 | 19 | 659 | 0.024026 | -4.8254e-06 | 3.5722e-10 | -0.0028966 | 8.9461e-07 | -6.9907e-11 | HDD
[100 empty] | 21 | 20 | 660 | -0.0001048 | 2.5328e-06 | -3.3212e-09 | 1.0522e-05 | -1.4019e-07 | 1.7068e-10 | CDD
[100 empty] | 21 | 21 | 661 | -0.00017042 | -9.7853e-09 | 7.2421e-13 | 7.0546e-08 | 8.1529e-10 | -1.2928e-12 | HDD
[100 empty] | 21 | 22 | 662 | 2.1428e-05 | -9.0007e-07 | 1.0304e-09 | -1.0209e-07 | 7.3748e-10 | -6.9465e-13 | CDD
[100 empty] | 21 | 23 | 663 | 0.049465 | 2.1427e-06 | -2.1149e-10 | -0.02695 | -1.4375e-06 | 1.4904e-10 | HDD
[100 empty] | 21 | 24 | 664 | 0.0025255 | 0.00012528 | -1.2549e-07 | -0.0026739 | -5.7283e-05 | 4.9671e-08 | CDD
[100 empty] | 21 | 25 | 665 | 0.023141 | 6.2595e-06 | -5.8003e-10 | -0.0062757 | -3.3477e-06 | 3.1489e-10 | HDD
[100 empty] | 21 | 26 | 666 | -0.01343 | 0.00017661 | -2.0941e-07 | 0.0074671 | -8.1393e-05 | 9.6813e-08 | CDD
[100 empty] | 21 | 27 | 667 | -4.3375 | 0.0020855 | -1.8208e-07 | 2.9699 | -0.0011385 | 9.7509e-08 | HDD
[100 empty] | 21 | 28 | 668 | 612.8053 | -8.9308 | 0.01734 | -384.2181 | 5.6096 | -0.010892 | CDD
[100 empty] | 21 | 29 | 669 | -10.3458 | 0.0047508 | -4.4212e-07 | 6.4205 | -0.0026488 | 2.4333e-07 | HDD
[100 empty] | 21 | 30 | 670 | -43.0081 | 0.33109 | -0.00049847 | 27.0141 | -0.20358 | 0.0003068 | CDD
[100 empty] | 21 | 31 | 671 | 0.74139 | 0.00022446 | -3.0221e-08 | 0.1982 | -0.00020177 | 2.8318e-08 | HDD
[100 empty] | 21 | 32 | 672 | 0.0012599 | -8.1488e-05 | 8.2968e-08 | -0.00045128 | 9.2509e-05 | -1.0179e-07 | CDD
[100 empty] | 22 | 1 | 673 | 0.91409 | 0.00019666 | -2.0458e-08 | -0.6265 | -0.00015426 | 1.531e-08 | HDD
[100 empty] | 22 | 2 | 674 | 0.4106 | 0.00010718 | -1.0818e-08 | -0.13253 | -4.5508e-05 | 4.3169e-09 | HDD
[100 empty] | 22 | 3 | 675 | 0.99967 | 0.00019933 | -2.129e-08 | -0.98534 | -0.00021915 | 2.2556e-08 | HDD
[100 empty] | 22 | 4 | 676 | 0.39223 | 8.1107e-05 | -8.6505e-09 | -0.15905 | -3.7604e-05 | 3.8512e-09 | HDD
[100 empty] | 22 | 5 | 677 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 22 | 6 | 678 | 0 | 0 | 0 | 0 | 0 | 0 | TDD
[100 empty] | 22 | 7 | 679 | -0.17007 | -1.45e-05 | 2.347e-09 | 0.022247 | -8.0949e-07 | -1.2807e-10 | HDD
[100 empty] | 22 | 8 | 680 | 0.0094563 | 1.394e-06 | -1.9272e-10 | -0.00095566 | -1.5487e-07 | 2.0744e-11 | HDD
[100 empty] | 22 | 9 | 681 | 0.11301 | 2.5182e-05 | -2.7025e-09 | -0.20901 | -3.2988e-05 | 3.8541e-09 | TDD
[100 empty] | 22 | 10 | 682 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 22 | 11 | 683 | -4.499e-06 | -9.5474e-09 | 7.55e-13 | 1.6537e-07 | 3.1836e-10 | -2.6187e-14 | HDD
[100 empty] | 22 | 12 | 684 | -0.024392 | 0.00012877 | -1.1945e-10 | 0 | 0 | 0 | HDD
[100 empty] | 22 | 13 | 685 | 0.17109 | 0.00062021 | -6.9737e-07 | -0.019753 | -4.9293e-05 | 5.3927e-08 | CDD
[100 empty] | 22 | 14 | 686 | 0.15197 | -0.035377 | 4.4941e-05 | -12.2365 | 0.20638 | -0.0002708 | CDD
[100 empty] | 22 | 15 | 687 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 22 | 16 | 688 | -0.18214 | 6.8151e-05 | -5.0922e-09 | -0.082385 | 4.2907e-05 | -1.8184e-09 | TDD
[100 empty] | 22 | 17 | 689 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 22 | 18 | 690 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 22 | 19 | 691 | 0.073327 | -5.7253e-06 | 3.4346e-10 | -0.0052051 | 5.7933e-07 | -3.97e-11 | HDD
[100 empty] | 22 | 20 | 692 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 22 | 21 | 693 | -0.00025807 | -2.9184e-08 | 2.7248e-12 | -1.6282e-07 | 1.4109e-10 | -1.3271e-14 | HDD
[100 empty] | 22 | 22 | 694 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 22 | 23 | 695 | 0.10698 | -7.1679e-06 | 7.1361e-10 | -0.065235 | 6.8743e-06 | -6.7901e-10 | HDD
[100 empty] | 22 | 24 | 696 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 22 | 25 | 697 | 0.064903 | 7.0226e-08 | 1.4844e-11 | -0.02383 | -3.3397e-08 | -2.0676e-11 | HDD
[100 empty] | 22 | 26 | 698 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 22 | 27 | 699 | -42.338 | 0.014375 | -1.0348e-06 | 25.8776 | -0.0085314 | 6.0884e-07 | HDD
[100 empty] | 22 | 28 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 22 | 29 | 701 | -34.2707 | 0.0085255 | -5.4224e-07 | 22.9412 | -0.0055185 | 3.477e-07 | HDD
[100 empty] | 22 | 30 | 702 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 22 | 31 | 703 | 8.1198 | -0.0037134 | 2.0105e-07 | -6.8864 | 0.0036734 | -2.0107e-07 | HDD
[100 empty] | 22 | 32 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 23 | 1 | 705 | 1.2169 | -0.00025598 | 1.5258e-08 | -0.62986 | 0.00012864 | -7.5211e-09 | HDD
[100 empty] | 23 | 2 | 706 | 0.8508 | -0.00017955 | 1.0735e-08 | -0.31736 | 6.504e-05 | -3.8174e-09 | HDD
[100 empty] | 23 | 3 | 707 | 1.0435 | -0.0002206 | 1.3244e-08 | -0.89861 | 0.00018748 | -1.1162e-08 | HDD
[100 empty] | 23 | 4 | 708 | 0.49525 | -0.00010516 | 6.3201e-09 | -0.21225 | 4.449e-05 | -2.6504e-09 | HDD
[100 empty] | 23 | 5 | 709 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 23 | 6 | 710 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 23 | 7 | 711 | -0.17505 | 3.9555e-05 | -2.4037e-09 | 0.012523 | -3.6049e-06 | 2.5372e-10 | TDD
[100 empty] | 23 | 8 | 712 | 0.039046 | -3.3874e-05 | 9.7387e-08 | -0.0038489 | 3.358e-06 | -9.5573e-09 | CDD
[100 empty] | 23 | 9 | 713 | -0.24098 | 5.1406e-05 | -3.0143e-09 | 0.038 | -1.0882e-05 | 7.6035e-10 | TDD
[100 empty] | 23 | 10 | 714 | 0.00047829 | 3.9619e-08 | -5.924e-12 | -7.0842e-06 | -5.3131e-10 | 8.3088e-14 | HDD
[100 empty] | 23 | 11 | 715 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 23 | 12 | 716 | -0.3925 | 0.00037302 | -2.3262e-08 | 0 | 0 | 0 | HDD
[100 empty] | 23 | 13 | 717 | -0.0062235 | 0.00014581 | -1.9287e-07 | 0.00041063 | -9.3276e-06 | 1.2318e-08 | CDD
[100 empty] | 23 | 14 | 718 | 0.055631 | -0.00054934 | 7.1117e-07 | -1.8659 | 0.012186 | -1.5788e-05 | CDD
[100 empty] | 23 | 15 | 719 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 23 | 16 | 720 | -1.341 | 0.00070141 | -5.2574e-08 | 4.146 | -0.0024703 | 1.9149e-07 | TDD
[100 empty] | 23 | 17 | 721 | 0.013701 | -2.4373e-06 | 1.2053e-10 | -0.096869 | 4.6399e-05 | -3.5392e-09 | HDD
[100 empty] | 23 | 18 | 722 | -0.0039125 | 0.00013218 | -2.1009e-07 | 0.0028082 | -8.5134e-05 | 1.3641e-07 | CDD
[100 empty] | 23 | 19 | 723 | 0.097102 | -1.6911e-05 | 8.7719e-10 | -0.0035715 | 3.7722e-07 | -8.3638e-12 | HDD
[100 empty] | 23 | 20 | 724 | -0.0006421 | 3.3554e-05 | -4.2263e-08 | 3.2609e-05 | -1.971e-06 | 2.4751e-09 | CDD
[100 empty] | 23 | 21 | 725 | -0.00022481 | -2.4321e-09 | 9.8392e-13 | 4.4637e-07 | -1.5796e-10 | 1.3322e-14 | HDD
[100 empty] | 23 | 22 | 726 | 8.9928e-05 | -2.4753e-06 | 3.5507e-09 | 2.0541e-07 | 4.4636e-10 | -1.9818e-12 | CDD
[100 empty] | 23 | 23 | 727 | 0.022966 | 1.6222e-05 | -1.5383e-09 | -0.0064879 | -1.1049e-05 | 1.0137e-09 | HDD
[100 empty] | 23 | 24 | 728 | -0.02214 | 0.00044124 | -6.1654e-07 | 0.011865 | -0.00022165 | 3.0798e-07 | CDD
[100 empty] | 23 | 25 | 729 | 0.10251 | -1.6182e-05 | 1.011e-09 | -0.053821 | 1.0934e-05 | -7.5032e-10 | HDD
[100 empty] | 23 | 26 | 730 | -0.023314 | 0.00034938 | -4.5583e-07 | 0.011006 | -0.0001489 | 1.8948e-07 | CDD
[100 empty] | 23 | 27 | 731 | -34.1581 | 0.012235 | -9.3892e-07 | 21.4933 | -0.0074018 | 5.6045e-07 | HDD
[100 empty] | 23 | 28 | 732 | 2.8033 | -0.015421 | 2.4884e-05 | -1.884 | 0.014646 | -2.2474e-05 | CDD
[100 empty] | 23 | 29 | 733 | 1.6654 | -9.3282e-05 | -6.2077e-09 | 2.1362 | -0.00074028 | 5.6505e-08 | HDD
[100 empty] | 23 | 30 | 734 | -1.4777 | 0.036236 | -7.0386e-05 | 0.73581 | -0.016582 | 3.4904e-05 | CDD
[100 empty] | 23 | 31 | 735 | 58.6513 | -0.012387 | 2.0861e-07 | -57.1973 | 0.012375 | -2.2175e-07 | HDD
[100 empty] | 23 | 32 | 736 | 4.7107 | -0.032125 | 5.2152e-05 | -5.0078 | 0.040673 | -6.3933e-05 | CDD
[100 empty] | 24 | 1 | 737 | 0.3276 | -4.2012e-06 | -2.3878e-09 | -0.16556 | -1.451e-06 | 1.5749e-09 | HDD
[100 empty] | 24 | 2 | 738 | 0.29975 | -7.0788e-06 | -2.1762e-09 | -0.12911 | 2.1685e-07 | 1.2854e-09 | HDD
[100 empty] | 24 | 3 | 739 | 0.31178 | 5.1693e-06 | -2.3208e-09 | -0.27348 | -5.9563e-06 | 2.197e-09 | HDD
[100 empty] | 24 | 4 | 740 | 0.15804 | -2.2336e-06 | -6.8577e-10 | -0.072132 | 1.8473e-06 | 2.3459e-10 | HDD
[100 empty] | 24 | 5 | 741 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 24 | 6 | 742 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 24 | 7 | 743 | -0.013999 | 1.108e-06 | 4.6618e-12 | 0.00025114 | -4.9371e-08 | 3.2894e-12 | TDD
[100 empty] | 24 | 8 | 744 | -0.0041049 | 4.1282e-06 | -3.6226e-10 | 0.00026532 | -3.8885e-07 | 4.1239e-11 | TDD
[100 empty] | 24 | 9 | 745 | -0.026502 | 1.1343e-06 | 2.3314e-11 | 0.001735 | -4.8929e-07 | 4.2056e-11 | HDD
[100 empty] | 24 | 10 | 746 | 0.00057258 | -1.4077e-09 | -7.5077e-14 | -7.8217e-06 | 3.0915e-11 | -1.0389e-16 | HDD
[100 empty] | 24 | 11 | 747 | 0.00049875 | -7.2872e-08 | 5.0265e-12 | -7.5058e-06 | 1.1337e-09 | -7.871e-14 | HDD
[100 empty] | 24 | 12 | 748 | 0.48496 | 0.00013005 | -5.1994e-09 | 0 | 0 | 0 | HDD
[100 empty] | 24 | 13 | 749 | -0.0017506 | 0.00025089 | -2.7094e-07 | 0.00013204 | -1.5825e-05 | 1.7199e-08 | CDD
[100 empty] | 24 | 14 | 750 | -0.024198 | -0.00078552 | 5.7625e-07 | 0.69833 | -0.0047238 | 5.6008e-06 | CDD
[100 empty] | 24 | 15 | 751 | 0.0082372 | 7.9806e-05 | -1.3323e-07 | -0.0055283 | -4.1033e-05 | 6.9771e-08 | CDD
[100 empty] | 24 | 16 | 752 | 3.2013 | -3.9908e-05 | 3.3804e-08 | -16.0773 | 0.0017039 | -2.79e-07 | HDD
[100 empty] | 24 | 17 | 753 | 0.22546 | -5.3031e-05 | 2.9281e-09 | -0.19775 | 7.4341e-05 | -3.9314e-09 | TDD
[100 empty] | 24 | 18 | 754 | -0.011103 | -3.6561e-05 | 7.065e-08 | 0.013513 | 0.00010884 | -1.8088e-07 | CDD
[100 empty] | 24 | 19 | 755 | 0.033168 | -7.3401e-06 | 5.469e-10 | -0.0037291 | 1.207e-06 | -9.6029e-11 | HDD
[100 empty] | 24 | 20 | 756 | 1.2155e-05 | 1.2003e-06 | -1.1199e-09 | 5.9527e-06 | -8.9112e-08 | 8.6235e-11 | CDD
[100 empty] | 24 | 21 | 757 | -0.00025361 | -2.8694e-09 | 5.2039e-13 | -2.6477e-07 | 1.9475e-10 | -1.5229e-14 | HDD
[100 empty] | 24 | 22 | 758 | -1.2939e-05 | -7.5383e-07 | 8.8471e-10 | 2.0409e-07 | -1.0446e-09 | 1.161e-12 | CDD
[100 empty] | 24 | 23 | 759 | 0.079962 | -4.8932e-06 | 3.1181e-10 | -0.029877 | -3.4822e-05 | 5.4887e-08 | HDD
[100 empty] | 24 | 24 | 760 | -0.00903 | 0.0002096 | -2.4639e-07 | 0.0074657 | -0.00012727 | 1.4947e-07 | CDD
[100 empty] | 24 | 25 | 761 | 0.077662 | -9.4107e-06 | 6.9388e-10 | -0.033357 | 4.9364e-06 | -3.7349e-10 | HDD
[100 empty] | 24 | 26 | 762 | 0.0020393 | 0.00010548 | -1.3112e-07 | -0.0015633 | -3.809e-05 | 4.8142e-08 | CDD
[100 empty] | 24 | 27 | 763 | -3.042 | 0.0015729 | -1.3676e-07 | 2.445 | -0.00091044 | 7.5624e-08 | HDD
[100 empty] | 24 | 28 | 764 | -42.2039 | 0.16647 | -0.00010795 | 27.5477 | -0.10628 | 6.9162e-05 | CDD
[100 empty] | 24 | 29 | 765 | -10.3751 | 0.0045684 | -4.0951e-07 | 6.453 | -0.0025343 | 2.2237e-07 | HDD
[100 empty] | 24 | 30 | 766 | -42.5676 | 0.32948 | -0.00049759 | 26.7524 | -0.20257 | 0.00030614 | CDD
[100 empty] | 24 | 31 | 767 | 3.3894 | -0.00081476 | 6.0902e-08 | -2.118 | 0.00073421 | -5.6064e-08 | HDD
[100 empty] | 24 | 32 | 768 | 190.9189 | -1.0482 | 0.0012357 | -190.1576 | 1.05 | -0.0012383 | CDD
[100 empty] | 25 | 1 | 769 | -0.0092584 | 3.04e-06 | -2.2985e-10 | 0.0071378 | -2.3437e-06 | 1.772e-10 | HDD
[100 empty] | 25 | 2 | 770 | -0.013823 | 4.5389e-06 | -3.4318e-10 | 0.0074595 | -2.4493e-06 | 1.8519e-10 | HDD
[100 empty] | 25 | 3 | 771 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 25 | 4 | 772 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 25 | 5 | 773 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 25 | 6 | 774 | 0 | 0 | 0 | 0 | 0 | 0 | TDD
[100 empty] | 25 | 7 | 775 | -0.0009434 | 3.0977e-07 | -2.3421e-11 | 0.00063743 | -2.093e-07 | 1.5825e-11 | HDD
[100 empty] | 25 | 8 | 776 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 25 | 9 | 777 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 25 | 10 | 778 | 1.696e-05 | -2.6831e-09 | 1.1416e-13 | -2.3142e-07 | 3.4138e-11 | -1.2496e-15 | HDD
[100 empty] | 25 | 11 | 779 | 0.00077085 | -1.5066e-07 | 8.6589e-12 | -1.9448e-06 | 3.3304e-10 | -1.6785e-14 | HDD
[100 empty] | 25 | 12 | 780 | 0.38025 | 0.00018028 | -1.0774e-08 | 0 | 0 | 0 | HDD
[100 empty] | 25 | 13 | 781 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 25 | 14 | 782 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 25 | 15 | 783 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 25 | 16 | 784 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 25 | 17 | 785 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 25 | 18 | 786 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 25 | 19 | 787 | 0.048259 | 1.0221e-05 | -1.4587e-09 | 0.018041 | -6.7098e-06 | 5.2042e-10 | HDD
[100 empty] | 25 | 20 | 788 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 25 | 21 | 789 | -0.0057678 | 1.2535e-06 | -7.6657e-11 | 1.2605e-05 | -3.37e-09 | 2.2518e-13 | HDD
[100 empty] | 25 | 22 | 790 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 25 | 23 | 791 | 1.1075 | -0.00020358 | 1.1216e-08 | -0.56607 | 9.9191e-05 | -5.2611e-09 | HDD
[100 empty] | 25 | 24 | 792 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 25 | 25 | 793 | 0.77047 | -0.00013927 | 7.4835e-09 | -0.2527 | 4.1231e-05 | -1.9962e-09 | HDD
[100 empty] | 25 | 26 | 794 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 25 | 27 | 795 | -112.3095 | 0.040499 | -3.1885e-06 | 70.5885 | -0.025112 | 1.9664e-06 | HDD
[100 empty] | 25 | 28 | 796 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 25 | 29 | 797 | -1.3249 | 0.00096713 | -8.3259e-08 | 3.3298 | -0.0011775 | 8.7752e-08 | HDD
[100 empty] | 25 | 30 | 798 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 25 | 31 | 799 | -1.7189 | 0.0010318 | -8.674e-08 | 4.7178 | -0.0016058 | 1.1904e-07 | HDD
[100 empty] | 25 | 32 | 800 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 26 | 1 | 801 | 0.018355 | -3.1152e-06 | 1.3875e-10 | -0.0099584 | 1.4917e-06 | -5.2653e-11 | HDD
[100 empty] | 26 | 2 | 802 | 0.032391 | -1.0045e-05 | 7.0275e-10 | -0.016425 | 5.399e-06 | -3.827e-10 | HDD
[100 empty] | 26 | 3 | 803 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 26 | 4 | 804 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 26 | 5 | 805 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 26 | 6 | 806 | 0 | 0 | 0 | 0 | 0 | 0 | TDD
[100 empty] | 26 | 7 | 807 | -0.0032779 | 1.0341e-06 | -7.3662e-11 | 0.00045971 | -1.9309e-07 | 1.5007e-11 | HDD
[100 empty] | 26 | 8 | 808 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 26 | 9 | 809 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 26 | 10 | 810 | -1.2154e-05 | 7.4566e-09 | -6.7396e-13 | 3.0461e-07 | -1.5037e-10 | 1.3093e-14 | HDD
[100 empty] | 26 | 11 | 811 | 0.00077045 | -1.5296e-07 | 8.9172e-12 | -2.3352e-06 | 4.6699e-10 | -2.7113e-14 | HDD
[100 empty] | 26 | 12 | 812 | 0.3945 | 0.00017568 | -1.0443e-08 | 0 | 0 | 0 | HDD
[100 empty] | 26 | 13 | 813 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 26 | 14 | 814 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 26 | 15 | 815 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 26 | 16 | 816 | 0.0083269 | -2.6855e-06 | 2.3587e-10 | -0.0063804 | 2.4554e-06 | -2.2087e-10 | HDD
[100 empty] | 26 | 17 | 817 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 26 | 18 | 818 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 26 | 19 | 819 | 0.047626 | 1.0837e-05 | -1.5068e-09 | 0.01813 | -6.7493e-06 | 5.23e-10 | HDD
[100 empty] | 26 | 20 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 26 | 21 | 821 | -0.0055204 | 1.1911e-06 | -7.274e-11 | 1.1662e-05 | -3.136e-09 | 2.1102e-13 | HDD
[100 empty] | 26 | 22 | 822 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 26 | 23 | 823 | 1.0905 | -0.00020261 | 1.1324e-08 | -0.55885 | 9.9629e-05 | -5.4055e-09 | HDD
[100 empty] | 26 | 24 | 824 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 26 | 25 | 825 | 0.88292 | -0.00018238 | 1.123e-08 | -0.32216 | 6.7384e-05 | -4.2483e-09 | HDD
[100 empty] | 26 | 26 | 826 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 26 | 27 | 827 | -119.082 | 0.042878 | -3.372e-06 | 74.7059 | -0.02656 | 2.0781e-06 | HDD
[100 empty] | 26 | 28 | 828 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 26 | 29 | 829 | -1.6704 | 0.00098195 | -8.044e-08 | 3.4773 | -0.0011526 | 8.2894e-08 | HDD
[100 empty] | 26 | 30 | 830 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 26 | 31 | 831 | -4.2308 | 0.001921 | -1.5713e-07 | 4.5085 | -0.0015559 | 1.1812e-07 | HDD
[100 empty] | 26 | 32 | 832 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 27 | 1 | 833 | 1.2169 | -0.00025598 | 1.5258e-08 | -0.62986 | 0.00012864 | -7.5211e-09 | HDD
[100 empty] | 27 | 2 | 834 | 0.8508 | -0.00017955 | 1.0735e-08 | -0.31736 | 6.504e-05 | -3.8174e-09 | HDD
[100 empty] | 27 | 3 | 835 | 1.0435 | -0.0002206 | 1.3244e-08 | -0.89861 | 0.00018748 | -1.1162e-08 | HDD
[100 empty] | 27 | 4 | 836 | 0.49525 | -0.00010516 | 6.3201e-09 | -0.21225 | 4.449e-05 | -2.6504e-09 | HDD
[100 empty] | 27 | 5 | 837 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 27 | 6 | 838 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 27 | 7 | 839 | -0.17505 | 3.9555e-05 | -2.4037e-09 | 0.012523 | -3.6049e-06 | 2.5372e-10 | TDD
[100 empty] | 27 | 8 | 840 | 0.039046 | -3.3874e-05 | 9.7387e-08 | -0.0038489 | 3.358e-06 | -9.5573e-09 | CDD
[100 empty] | 27 | 9 | 841 | -0.24098 | 5.1406e-05 | -3.0143e-09 | 0.038 | -1.0882e-05 | 7.6035e-10 | TDD
[100 empty] | 27 | 10 | 842 | 0.00047829 | 3.9619e-08 | -5.924e-12 | -7.0842e-06 | -5.3131e-10 | 8.3088e-14 | HDD
[100 empty] | 27 | 11 | 843 | 0 | 0 | 0 | 0 | 0 | 0 | HDD
[100 empty] | 27 | 12 | 844 | -0.3925 | 0.00037302 | -2.3262e-08 | 0 | 0 | 0 | HDD
[100 empty] | 27 | 13 | 845 | -0.0062235 | 0.00014581 | -1.9287e-07 | 0.00041063 | -9.3276e-06 | 1.2318e-08 | CDD
[100 empty] | 27 | 14 | 846 | 0.055631 | -0.00054934 | 7.1117e-07 | -1.8659 | 0.012186 | -1.5788e-05 | CDD
[100 empty] | 27 | 15 | 847 | 0 | 0 | 0 | 0 | 0 | 0 | CDD
[100 empty] | 27 | 16 | 848 | -1.341 | 0.00070141 | -5.2574e-08 | 4.146 | -0.0024703 | 1.9149e-07 | TDD
[100 empty] | 27 | 17 | 849 | 0.013701 | -2.4373e-06 | 1.2053e-10 | -0.096869 | 4.6399e-05 | -3.5392e-09 | HDD
[100 empty] | 27 | 18 | 850 | -0.0039125 | 0.00013218 | -2.1009e-07 | 0.0028082 | -8.5134e-05 | 1.3641e-07 | CDD
[100 empty] | 27 | 19 | 851 | 0.097102 | -1.6911e-05 | 8.7719e-10 | -0.0035715 | 3.7722e-07 | -8.3638e-12 | HDD
[100 empty] | 27 | 20 | 852 | -0.0006421 | 3.3554e-05 | -4.2263e-08 | 3.2609e-05 | -1.971e-06 | 2.4751e-09 | CDD
[100 empty] | 27 | 21 | 853 | -0.00022481 | -2.4321e-09 | 9.8392e-13 | 4.4637e-07 | -1.5796e-10 | 1.3322e-14 | HDD
[100 empty] | 27 | 22 | 854 | 8.9928e-05 | -2.4753e-06 | 3.5507e-09 | 2.0541e-07 | 4.4636e-10 | -1.9818e-12 | CDD
[100 empty] | 27 | 23 | 855 | 0.022966 | 1.6222e-05 | -1.5383e-09 | -0.0064879 | -1.1049e-05 | 1.0137e-09 | HDD
[100 empty] | 27 | 24 | 856 | -0.02214 | 0.00044124 | -6.1654e-07 | 0.011865 | -0.00022165 | 3.0798e-07 | CDD
[100 empty] | 27 | 25 | 857 | 0.10251 | -1.6182e-05 | 1.011e-09 | -0.053821 | 1.0934e-05 | -7.5032e-10 | HDD
[100 empty] | 27 | 26 | 858 | -0.023314 | 0.00034938 | -4.5583e-07 | 0.011006 | -0.0001489 | 1.8948e-07 | CDD
[100 empty] | 27 | 27 | 859 | -34.1581 | 0.012235 | -9.3892e-07 | 21.4933 | -0.0074018 | 5.6045e-07 | HDD
[100 empty] | 27 | 28 | 860 | 2.8033 | -0.015421 | 2.4884e-05 | -1.884 | 0.014646 | -2.2474e-05 | CDD
[100 empty] | 27 | 29 | 861 | 1.6654 | -9.3282e-05 | -6.2077e-09 | 2.1362 | -0.00074028 | 5.6505e-08 | HDD
[100 empty] | 27 | 30 | 862 | -1.4777 | 0.036236 | -7.0386e-05 | 0.73581 | -0.016582 | 3.4904e-05 | CDD
[100 empty] | 27 | 31 | 863 | 58.6513 | -0.012387 | 2.0861e-07 | -57.1973 | 0.012375 | -2.2175e-07 | HDD
[100 empty] | 27 | 32 | 864 | 4.7107 | -0.032125 | 5.2152e-05 | -5.0078 | 0.040673 | -6.3933e-05 | CDD
Note on E3: Michel Parent: This table needs to be updated when new coefficents are produced or when the equations are updated.
Note on AL3: Michel Parent: This table needs to be updated whenever there is a change in the Table 5 of the code or when a Base (i.e. Reference) value changes for the system. It may need to be changed even if the coefficients don't change.
Note on BP3: Michel Parent: Valeurs à mettre à jour lorsque la réglementation des appareils est modifiée.
Note on BT16: Michel Parent: Valeurs à mettre à jour lorsque la réglementation des appareils est modifiée. Les valeurs négatives réfèrent à des appareils don’t le rendement est défini à même la feuille HVAC-CVCA au niveau des lignes cachées.e
Note on BX3: Michel Parent: This table only needs to be changed when there is a major update to the coefficients where the numeric value attached to a control logic is modified.
Note on DC2: Michel Parent: Tableau des coefficients. Ce tableau doit être mis à jour lorsque les coefficients sont modifiés.
Note on EI3: Michel Parent: Valeurs à mettre à jour lorsque la réglementation des appareils est modifiée. Les valeurs négative réfèrent à des rendements définis au niveau de la feuille SWH-CES.

## Minimum efficiencies entries (hidden)
Ranges
Sub-System | [6 empty] | System
Split System <= 19 (65000) | 4.395 | SEER | Table 5.2.12.1 - Heating |  |  | Minimum | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
Single-package systems <= 19 (65000) | 4.102 | SEER | Electric boilers | 100% |  | ToV1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
All phases > 19 (65000) and < 73 (250000) | 2.8421 | EER | Gas-fired boilers, < 88 kW | 85% | AFUE | ToV2 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.4 | 0.3
Air conditioners, all phases, split and single package >= 19 kW and < 40 kW, electric resistance heating section | 3.28 | COP | Gas-fired boilers, >= 88 kW and < 733 kW | 83% | Et | ToV3 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.2 | 0.1 | 0.1 | 0.2 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Air conditioners, all phases, split and single package >= 19 kW and < 40 kW, other heating section | 3.22 | COP | Gas-fired boilers, >= 733 kW | 83.3% | Ec | ToV4 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Air conditioners, all phases, split and single package >= 40 kW and < 70 kW, electric resistance heating section | 3.22 | COP | Oil-fired boilers, < 88 kW | 84.7% | AFUE | ToV5 | 0.5 | 0.2 | 0.73026 | 0.73026 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.86 | 0.5 | 0.5 | 0.86 | 0.86 | 0.5
Air conditioners, all phases, split and single package >= 40 kW and < 70 kW, other heating section | 3.16 | COP | Oil-fired boilers, >= 88 kW and < 733 kW | 83.4% | Et | ToV6 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207 | 0.207
Air conditioners, all phases, split and single package >= 70 kW and < 223 kW, electric resistance heating section | 2.93 | COP | Oil-fired boilers, >= 733 kW | 85.8% | Ec | ToV7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air conditioners, all phases, split and single package >= 70 kW and < 223 kW, electric resistance heating section | 2.87 | COP | Oil-fired boilers, residulal (No.5 or No.6 oil) and other, < 88 kW | 84.7% | AFUE | ToV8 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Air conditioners, all phases, split and single package >= 223 kW, electric resistance heating section | 2.84 | COP | Oil-fired boilers, residulal (No.5 or No.6 oil) and other, >= 88 kW and < 733 kW | 83.4% | Et | ToV9 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011 | 0.3011
Air conditioners, all phases, split and single package >= 223 kW, other heating section | 2.78 | COP | Oil-fired boilers, residulal (No.5 or No.6 oil) and other, >= 733 kW | 85.8% | Ec | ToV10 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 6 | 0.1 | 0.1 | 6 | 6 | 6 | 6 | 0.1 | 6 | 6 | 6 | 0.1 | 6 | 6 | 6 | 6 | 6
Heat Pumps >= 19 kW and < 40 kW, electric resistance heating section, split and single | 3.22 | COP | Gas-fired warm-air furnaces, <= 117.23 kW | 92.4% | AFUE | ToV11 | 0.1 | 0.1 | 11 | 11 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 6 | 6 | 6 | 6 | 0.1 | 6 | 6 | 6 | 0.1 | 0.1 | 6 | 0.1 | 6 | 0.1
Heat Pumps >= 19 kW and < 40 kW, other heating section, split and single | 3.16 | COP | Gas-fired warm-air furnaces, > 117.23 kW | 81% | Et | ToV12 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Heat Pumps >= 40 kW and < 70 kW, electric resistance heating section, split and single | 3.1 | COP | Gas-fired duct furnaces, <= 117.23 kW | 81% | Et | ToV13 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Heat Pumps >= 40 kW and < 70 kW, otherheating section, split and single | 3.04 | COP | Gas-fired unit heaters, <= 117.23 kW | 82% | Et | ToV14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Pumps >= 70 kW, electric resistance heating section, split and single | 2.78 | COP | Oil-fired warm-air furnaces, <= 66 kW | 84.5% | Et | ToV15 | 0.76117 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Pumps >= 70 kW, other heating section, split and single | 2.72 | COP | Oil-fired warm-air furnaces, > 66 kW | 81.3% | Et | ToV16 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Pumps >= 19 kW and < 70 kW in cooling mode at 8.3 ⁰C db / 6.1 ⁰C wb | 3.3 | COP | Oil-fired duct furnaces or unit heaters | 81% | Et | ToV17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Pumps >= 19 kW and < 70 kW in cooling mode at 8.3 ⁰C db / -9.4 ⁰C wb | 2.25 | COP |  |  |  | ToV18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Pumps >= 70 kW in cooling mode at 8.3 ⁰C db / 6.1 ⁰C wb | 3.2 | COP |  |  |  | ToV19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Heat Pumps >= 70 kW in cooling mode at 8.3 ⁰C db / -9.4 ⁰C wb | 2.05 | COP |  |  |  | ToV20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SPVAC and SPVHP in cooling mode < 19 kW | 2.93 | EER |  |  |  | ToV21 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SPVAC and SPVHP in cooling mode >= 19 kW and < 40 kW | 2.7835 | EER |  |  |  | ToV22 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
SPVAC and SPVHP in cooling mode >= 40 kW and < 70 kW | 2.5198 | EER |  |  |  | ToV23 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
SPVHP in heating mode < 19 kW | 3.1 | COP |  |  |  | ToV24 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
SPVHP in heating mode >= 19 kW and < 40 kW | 3 | COP |  |  |  | ToV25 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
SPVHP in heating mode >= 40 kW and < 70 kW | 2.9 | COP |  |  |  | ToV26 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
Evaporatively cooled <= 19 (65000) | 3.54 | COP |  |  |  | ToV27 | 0.79543 | 0.78485 | 0.78312 | 0.78156 | 0.78635 | 0.78339 | 0.79151 | 0.79 | 0.78635 | 0.7818 | 0.77853 | 0.78158 | 0.79807 | 0.77154 | 0.77094 | 0.77094 | 0.77 | 0.77 | 0.62164 | 0.77 | 0.77 | 0.77543 | 0.78514 | 0.76654 | 0.79111 | 0.79121 | 0.78514
Evaporatively cooled and water evaporatively cooled, split and single-package >= 19 kW and < 40 kW electric resistance heating section | 3.37 | COP |  |  |  | ToV28 | 0.79241 | 0.8 | 0.68748 | 0.72358 | 0.76265 | 0.76265 | 0.79 | 0.76265 | 0.76265 | 0.8 | 0.76265 | 0.8 | 0.8 | 0.79123 | 0.75062 | 0.75062 | 0.8 | 0.78 | 0.62164 | 0.79 | 0.79 | 0.68748 | 0.75339 | 0.78615 | 0.72358 | 0.72358 | 0.75339
Evaporatively cooled and water evaporatively cooled, split and single-package >= 19 kW and < 40 kW other heating section | 3.31 | COP |  |  |  | ToV29 | 0.79142 | 0.79903 | 0.78308 | 0.7821 | 0.79446 | 0.79446 | 0.79446 | 0.79446 | 0.79446 | 0.79946 | 0.79446 | 0.79446 | 0.79131 | 0.79075 | 0.76656 | 0.76656 | 0.77 | 0.77 | 0.7792 | 0.79 | 0.79 | 0.78308 | 0.76656 | 0.79106 | 0.62004 | 0.61885 | 0.76656
Evaporatively cooled and water evaporatively cooled, split and single-package >= 40 kW and < 70 kW electric resistance heating section | 3.22 | COP |  |  |  | ToV30 | 0.77744 | 0.79399 | 0.76797 | 0.76057 | 0.8 | 0.8 | 0.78295 | 0.79516 | 0.76929 | 0.79656 | 0.8 | 0.8 | 0.77572 | 0.8 | 0.77344 | 0.77344 | 0.8 | 0.8 | 0.8 | 0.78 | 0.78 | 0.76797 | 0.78415 | 0.78342 | 0.76057 | 0.76057 | 0.78415
Evaporatively cooled and water evaporatively cooled, split and single-package >= 40 kW and < 70 kW other heating section | 3.16 | COP |  |  |  | ToV31 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5
Water evaporatively cooled air conditioners, split and single-packaged >= 70 kW electric resistance heating section | 3.22 | COP |  |  |  | ToV32 | 0.8 | 0.8 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | 0.49661 | 0.5 | 0.5 | 0.5 | 0.49 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5 | 0.5 | 0.5 | 0.8 | 0.5
Water evaporatively cooled air conditioners, split and single-packaged >= 70 kW other heating section | 3.16 | COP |  |  |  | Maximum | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27
Air conditioner, air-cooled, electric or no heating - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB - >=19 <40 | 3.2816 |  |  |  |  | ToV1 | 0.9 | 0.9 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.7 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Air conditioner, air-cooled, electric or no heating - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB | 3.223 |  |  |  |  | ToV2 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
Air conditioner, air-cooled, electric or no heating - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB | 2.93 |  |  |  |  | ToV3 | 0.6 | 0.6 | 0.55 | 0.55 | 0.6 | 0.34 | 0.6 | 0.4 | 0.55 | 0.6 | 0.45 | 0.6 | 0.6 | 0.6 | 0.55 | 0.55 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.5 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Air conditioner, air-cooled, electric or no heating - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB - >= 223 (>= 760) | 2.8421 |  |  |  |  | ToV4 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
Air conditioner, water & evaporatively cooled, electric or no heating - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | 3.3695 |  |  |  |  | ToV5 | 1 | 0.42528 | 0.94 | 0.94 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Air conditioner, water & evaporatively cooled, electric or no heating - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | 3.223 |  |  |  |  | ToV6 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604 | 0.604
Air conditioner, water & evaporatively cooled, electric or no heating - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | 3.223 |  |  |  |  | ToV7 | 9 | 9 | 6.8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 6 | 9 | 9 | 9 | 6 | 9
Heat pump, electric or no heating - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | 3.223 |  |  |  |  | ToV8 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 6 | 6 | 8 | 6 | 5 | 6 | 6 | 6 | 3.7 | 4 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Heat pump, electric or no heating - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | 3.1058 |  |  |  |  | ToV9 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 5 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Heat pump, electric or no heating - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | 2.7835 |  |  |  |  | ToV10 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 50 | 50 | 38 | 40 | 40 | 40 | 50 | 40 | 40 | 40 | 50 | 40 | 40 | 40 | 40 | 40
Air conditioner, air-cooled, all other heating section - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB - >=19 <40 | 3.223 |  |  |  |  | ToV11 | 50 | 50 | 40 | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 40 | 40 | 40 | 50 | 40 | 40 | 40 | 50 | 50 | 40 | 50 | 40 | 50
Air conditioner, air-cooled, all other heating section - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB | 3.1644 |  |  |  |  | ToV12 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 7 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Air conditioner, air-cooled, all other heating section - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB | 2.8714 |  |  |  |  | ToV13 | 8 | 8 | 6 | 8 | 6 | 6 | 10 | 6 | 10 | 10 | 7 | 10 | 10 | 10 | 10 | 10 | 7 | 6 | 10 | 10 | 10 | 6 | 10 | 10 | 10 | 10 | 10
Air conditioner, air-cooled, all other heating section - SP-A, RC-A, RCU-A-C, SPY-A, RCY-A, RCU-A-CB, RCUY-A-CB - >= 223 (>= 760) | 2.7835 |  |  |  |  | ToV14 | 1 | 1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 1 | 1 | 0.1 | 1 | 0.1 | 0.1 | 0.1 | 1 | 0.1 | 1 | 1 | 1 | 1 | 0.1 | 0.08 | 1 | 1 | 1 | 0.08
Air conditioner, water & evaporatively cooled, all other heating section - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | 3.3109 |  |  |  |  | ToV15 | 0.8005 | 0.80072 | 0.95 | 0.95 | 0.95 | 0.8 | 0.95 | 0.95 | 0.95 | 0.80004 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.95 | 0.9 | 0.95 | 0.95 | 0.95
Air conditioner, water & evaporatively cooled, all other heating section - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | 3.1644 |  |  |  |  | ToV16 | 0.92987 | 0.85108 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.93 | 0.84931 | 0.93 | 0.93 | 0.93 | 0.26015 | 0.11724 | 0.11724 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.93 | 0.12 | 0.11724 | 0.93 | 0.93 | 0.12
Air conditioner, water & evaporatively cooled, all other heating section - SP-E, SP-W, RC-E, RC-W, SPY-E, SPY-W, RCY-E, RCY-W, RCU-E-C, RCU-W-C, RCU-E-CB, RCU-W-CB, RCUY-E-CB, RCUY-W-CB | 3.1644 |  |  |  |  | ToV17 | 0.9 | 0.8 | 0.99 | 0.99 | 0.9 | 0.8 | 0.9 | 0.9 | 0.9 | 0.6 | 0.6 | 0.9 | 0.7 | 0.9 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.9 | 0.99 | 0.99 | 0.9 | 0.99 | 0.99 | 0.99 | 0.99
Heat pump, all other heating section - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | 3.1644 |  |  |  |  | ToV18 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
Heat pump, all other heating section - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | 3.0472 |  |  |  |  | ToV19 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Heat pump, all other heating section - HSP-A, HRC-A-C, HRCU-A-C, HRC-A-CB, HRCU-A-CB | 2.7249 |  |  |  |  | ToV20 | 9 | 9 | 9 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Large condensing units - RCU-A | 2.9593 |  |  |  |  | ToV21 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Large condensing units - RCU-E, RCU-W | 3.8383 | COP |  |  |  | ToV22 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
Condensing unit - Air-cooled >= 73 (250000) | 2.96 | COP |  |  |  | ToV23 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Condensing unit - Water evaporatively cooled >= 73 (250000) | 3.84 | COP |  |  |  | ToV24 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Ground or water source heat pumps < 35 (119500) - open systems | 4.75 |  |  |  |  | ToV25 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
Ground or water source heat pumps < 35 (119500) - closed systems | 3.93 |  |  |  |  | ToV26 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99
Internal water-loop heat pumps < 40 (136500) | 3.52 |  |  |  |  | ToV27 | 0.85549 | 0.8 | 0.89131 | 0.89921 | 0.84728 | 0.8 | 0.82523 | 0.842 | 0.84779 | 0.84981 | 0.85102 | 0.84846 | 0.80202 | 0.98574 | 0.95884 | 0.95884 | 0.96 | 0.96 | 0.8 | 1.02 | 1.02 | 0.94997 | 1.0719 | 1.0964 | 0.86834 | 0.86618 | 1.0719
Water-cooled air conditioners < 19 (65000) | 3.54 | COP |  |  |  | ToV28 | 0.80515 | 0.82308 | 0.8 | 0.8 | 0.80113 | 0.80113 | 0.81 | 0.80113 | 0.81 | 0.81584 | 0.80113 | 0.81346 | 0.8357 | 0.8 | 0.8 | 0.8 | 0.81 | 0.812 | 0.8 | 0.8 | 0.8 | 0.8505 | 0.8505 | 0.8 | 0.8 | 0.8 | 0.8505
Water-cooled air conditioners >= 19 kW and < 40 kW electric resistance heating (or none) | 3.37 | COP |  |  |  | ToV29 | 0.86746 | 0.81539 | 0.90771 | 0.91766 | 0.8544 | 0.8544 | 0.8544 | 0.8544 | 0.8544 | 0.80076 | 0.81 | 0.81 | 0.83112 | 1.0477 | 1.0298 | 1.0298 | 1.03 | 1.03 | 0.84526 | 1.05 | 1.05 | 1.0405 | 1.0405 | 1.1301 | 1.2211 | 1.3865 | 1.0405
Water-cooled air conditioners >= 19 kW and < 40 kW all other | 3.31 | COP |  |  |  | ToV30 | 0.8333 | 0.808 | 0.81361 | 0.81676 | 0.80354 | 0.80354 | 0.82663 | 0.85575 | 0.83598 | 0.8041 | 0.80354 | 0.80354 | 0.83242 | 0.82226 | 0.84046 | 0.84046 | 0.84 | 0.8 | 0.80278 | 0.81 | 0.81 | 0.82177 | 0.82177 | 0.81362 | 0.81676 | 0.81676 | 0.82177
Water-cooled air conditioners >= 40 kW and < 70 kW electric resistance heating (or none) | 3.22 | COP |  |  |  | ToV31 | 0.81234 | 0.80338 | 0.51973 | 0.51311 | 0.51138 | 0.50395 | 0.50709 | 0.51017 | 0.50268 | 0.8016 | 0.50455 | 0.50163 | 0.51014 | 0.51827 | 0.51816 | 0.51816 | 0.5 | 0.5 | 0.52111 | 0.50962 | 0.50962 | 0.51041 | 0.51041 | 0.51187 | 0.58102 | 0.88011 | 0.51041
Water-cooled air conditioners >= 40 kW and < 70 kW all other | 3.16 | COP |  |  |  | ToV32 | 0.80684 | 0.80165 | 0.8623 | 0.56038 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.80086 | 0.9 | 0.50085 | 0.50753 | 0.5 | 0.50668 | 0.50668 | 0.52 | 0.52 | 0.9 | 0.9 | 0.9 | 0.51009 | 0.51009 | 0.50359 | 0.56038 | 0.86038 | 0.51009
Water-cooled air conditioners >= 70 kW electric resistance heating (or none) | 3.22 | COP
Water-cooled air conditioners >= 70 kW all other | 3.16 | COP
Direct-expansion ground-source heat pumps <= 21 (71700) | 3.809
PTAC and PTHP air-cooled electrically operated - Electrically Operated | -1
PTHP in cooling mode (Standard rating) | -2
PTHP in heating mode (Standard rating) | -3
Room air conditioners with reserve cycle with louvered sides < 10.55 (36000) | 2.4905
Room air conditioners with reserve cycle without louvered sides < 10.55 (36000) | 2.344
Room air conditioners without reverse cycle < 10.55 (36000) | 2.4905
Room air conditioners with louvered sides < 1.8 kW | 2.84
Room air conditioners with louvered sides >= 1.8 kW and < 2.3 kW | 2.84
Room air conditioners with louvered sides >= 2.3 kW and < 4.1 kW | 2.87
Room air conditioners with louvered sides >= 4.1 kW and < 5.9 kW | 2.84
Room air conditioners with louvered sides >= 5.9 kW | 2.49
Room air conditioners without louvered sides < 2.3 kW | 2.64
Room air conditioners wothout louvered sides >= 2.3 kW and < 5.9 kW | 2.49
Room air conditioners without louvered sides >= 5.9 kW | 2.49
Room air conditioner heat pumps with louvered sides < 5.9 kW | 2.65
Room air conditioner heat pumps with louvered sides < 5.9 kW | 2.49
Room air conditioner heat pumps without louvered sides < 4.1 | 2.49
Room air conditioner heat pumps without louvered sides >= 4.1 | 2.34
Room air conditioner casement only | 2.55
Room air conditioner casement slider | 2.78
Air-cooled < 19 (65000) | 2.09
Air-cooled < 19 (65000) and < 70 (240000) | 1.99
Air-cooled >= 70 (240000) | 1.79
Water-cooled < 19 (65000) | 2.49
Water-cooled >= 19 (65000) and < 70 (240000) | 2.39
Water-cooled >= 70 (240000) | 2.29
Water-cooled with fluid economizer < 19 (65000) | 2.44
Water-cooled with fluid economizer >= 19 (65000) and < 70 (240000) | 2.34
Water-cooled with fluid economizer >= 70 (240000) | 2.24
Glycol-cooled < 19 (65000) | 2.39
Glycol-cooled >= 19 (65000) and 70 (240000) | 2.04
Glycol-cooled >= 70 (240000) | 1.99
Glycol-cooled with fluid economizer < 19 (65000) | 2.34
Glycol-cooled with fluid economizer >= 19 (65000) and < 70 (240000) | 1.99
Glycol-cooled with fluid economizer >= 70 (240000) | 1.94
Chilled water air handler < 19 (65000) | 6.06
Chilled water air handler >= 19 (65000) and < 70 (240000) | 7.06
Chilled water air handler >= 70 (240000) | 9.06
Air cooled, with condenser, electrically operated | 2.8
Air cooled, without condenser, electrically operated | 3.1
Water cooled, electrically operated, positive displacement (reciprocating) | 4.2
Water cooled, electrically operated, positive displacement (rotary screw and scroll) < 150 Tons | 4.45
Water cooled, electrically operated, positive displacement (rotary screw and scroll) >= 150 Tons & < 300 Tons | 4.9
Water cooled, electrically operated, positive displacement (rotary screw and scroll) >= 300 Tons | 5.5
Water cooled, electrically operated, positive displacement (centrifugal) < 150 Tons | 5
Water cooled, electrically operated, positive displacement (centrifugal) >= 150 Tons & < 300 Tons | 5.55
Water cooled, electrically operated, positive displacement (centrifugal) >= 300 Tons | 6.1
Air cooled absorption single effect | 0.6
Water cooled absorption single effect | 0.7
Absorption double effect, indirect-fired | 1
Absorption double effect, direct-fired | 1
Note on B9: Michel Parent: Valeurs à mettre à jour lorsque la réglementation des appareils est modifiée. Les valeurs négatives réfèrent à des appareils don’t le rendement est défini à même la feuille HVAC-CVCA au niveau des lignes cachées.
Note on F10: Michel Parent: Valeurs à mettre à jour lorsque la réglementation des appareils est modifiée.

## Climate-Climat
Climate Zones
City / Location | Province/Territory | Zone
Vancouver | Br. Columbia | 4
Abbotsford | Br. Columbia | 5
Tofino | Br. Columbia | 5
Penticton | Br. Columbia | 5
Penticton | Br. Columbia | 5
Port Hardy | Br. Columbia | 5
Windsor | Ontario | 5
Kamloops | Br. Columbia | 5
Toronto | Ontario | 5
Castlegar | Br. Columbia | 5
Victoria | Br. Columbia | 5
Prince Rupert | Br. Columbia | 6
Halifax | Nova Scotia | 6
Yarmouth | Nova Scotia | 6
London | Ontario | 6
Trenton | Ontario | 6
Montreal (Dorval) | Quebec | 6
Greenwood | Nova Scotia | 6
Terrace | Br. Columbia | 6
Ottawa | Ontario | 6
Charlottetown | P.E.I. | 6
St. Hubert | Quebec | 6
Lethbridge | Alberta | 6
Cranbrook | Br. Columbia | 6
Fredericton | New Brunswick | 6
Truro | Nova Scotia | 6
Summerside | P.E.I. | 6
Medicine Hat | Alberta | 6
Moncton | New Brunswick | 6
Mount Forest | Ontario | 6
Saint John | New Brunswick | 6
St John's | Newfoundland | 6
Sherbrooke | Quebec | 6
Stephenville | Newfoundland | 6
Williams Lake | Br. Columbia | 7A
Sault Ste. Marie | Ontario | 7A
Calgary | Alberta | 7A
Gander | Newfoundland | 7A
Quebec | Quebec | 7A
Prince George | Br. Columbia | 7A
North Bay | Ontario | 7A
Edmonton | Alberta | 7A
Sudbury | Ontario | 7A
Estevan | Saskatchewan | 7A
Swift Current | Saskatchewan | 7A
Mont Joli | Quebec | 7A
Charlo (Campbellton) | New Brunswick | 7A
Riviere-du-Loup | Quebec | 7A
Thunder Bay | Ontario | 7A
Red Deer | Alberta | 7A
Regina | Saskatchewan | 7A
Bagotville | Quebec | 7A
Kenora | Ontario | 7A
Winnipeg | Manitoba | 7A
Saskatoon | Saskatchewan | 7A
Grande Prairie | Alberta | 7B
Fort St. John | Br. Columbia | 7B
Brandon | Manitoba | 7B
Dauphin | Manitoba | 7B
Timmins | Ontario | 7B
Sept-Iles | Quebec | 7B
Val d'Or | Quebec | 7B
Battle Harbour (St Anthony) | Newfoundland | 7B
Peace River | Alberta | 7B
Kapuskasing | Ontario | 7B
Prince Albert | Saskatchewan | 7B
Fort McMurray | Alberta | 7B
Cartwright (Happy Valley - Goose Bay) | Newfoundland | 7B
Happy Valley - Goose Bay | Newfoundland | 7B
The Pas | Manitoba | 7B
Whitehorse | Yukon | 7B
Whitehorse | Yukon | 7B
Fort Nelson | Br. Columbia | 8
Big Trout Lake | Ontario | 8
Fort Smith | Northwest Terr. | 8
Thompson | Manitoba | 8
Uranium City | Saskatchewan | 8
Wabush | Newfoundland | 8
Nitchequon | Quebec | 8
Kuujjuarapik | Quebec | 8
Schefferville | Quebec | 8
Yellowknife | Northwest Terr. | 8
Kuujuaq | Quebec | 8
Norman Wells | Northwest Terr. | 8
Churchill | Manitoba | 8
Inuvik | Northwest Terr. | 8
Iqualuit | Nunavut | 8
Inuvik (NWT) | Yukon | 8
Chesterfield Inlet | Nunavut | 8
Coral Harbour | Nunavut | 8
Cambridge Bay | Nunavut | 8

## HVAC-CVCA Report-Rapport
Statement of Compliance - National Energy Code of Canada for Buildings 2020 Summary Report to NECB Part 5 - Simple Trade-Off
Project Name: |  |  | Building Permit Number (Completed Internally) | Date:
Project Address:
Applicant Name:
Applicant Address: |  |  |  | Applicant Phone:
General information
Date of plans: |  | Building conditioned Floor area (m2):
Climate zone: |  | Number of HVAC Systems in the Building:
Statement of Compliance - National Energy Code for Buildings
This Compliance Report lists the building features as per the actual building permit drawings and specifications in accordance with Part 5.3 of the National Energy Code for Buildings.
Document Author: |  |  | Date:
Signature:
Summary compliance results
Overall HVAC-TOI: 0.035180
Number of Compliant Systems: 1
Number of non-Compliant Systems: 0
HVAC system deemed to comply with Section 5.3
For projects requiring Professional involvement under Division C of the National Buildign Code (AB Edition), the responsible professional on record must stamp & sign this document. For projects not requiring Professional involvement, the individual responsible for compliance should check and complete Check 2 below.
Check 1
1. I hereby affirm I am eligible, under the provisions of the authorities having jurisdiction, to sign this document as the person responsible for its preparation; and I am a registered professional engineer or architect in the Province of Alberta
Check 2
2. I affirm that I am eligible to sign this document as the person responsible for its preparation for the following reason: _____________________________________________________________________________
Coordinating Professional:
Signature:
Date:
STAMP REQUIRED
for projects requiring professional involvement under the Alberta Building Code
Part 5: Heating, Ventilating & A/C Systems
Trade-Off Compliance Report
(2016/02)

## SWH-CES Report-Rapport
Statement of Compliance - National Energy Code of Canada for Buildings 2020 Summary Report to NECB Part 6 - Simple Trade-Off
Project Name: |  |  | Building Permit Number (Completed Internally) | Date:
Project Address:
Applicant Name:
Applicant Address: |  |  |  | Applicant Phone:
General information
Date of plans: |  | Building conditioned Floor area (m2): | 0
Climate zone: | Zone 7B | Number of SWH Systems in the Building: | 1
Statement of Compliance - National Energy Code for Buildings
This Compliance Report lists the building features as per the actual building permit drawings and specifications in accordance with Part 6.3 of the National Energy Code for Buildings.
Document Author: |  |  | Date:
Signature:
Summary Compliance Results
Overall SWH-TOI: 0.00
Number of Compliant Systems: 1
Number of non-Compliant Systems: 0
The SWH system is deemed to comply with Section 6.3
For projects requiring Professional involvement under Division C of the National Building Code (AB Edition), the responsible professional on record must stamp & sign this document. For projects not requiring Professional involvement, the individual responsible for compliance should check and complete Check 2 below.
Check 1
1. I hereby affirm that I am eligible, under the provisions of the authorities having jurisdiction, to sign this document as the person responsible for its preparation; and I am licensed as an engineer or architect permitted to practice in the Province of Alberta.
Check 2
2. I affirm that I am eligible to sign this document as the person responsible for its preparation for the following reason: ________________________________________________________________
Coordinating Professional:
Signature:
Date:
STAMP REQUIRED
for projects requiring professional involvement under the Alberta Building Code
Part 6: Service Water Heating Systems
Trade-off Compliance Report
(2016/02)

## Help-Aide
HVAC Help Table
System Type | Choose from the list of 27 HVAC System Types ID available in the drop down list and as provided in Table 5.3.1.1 of the NECB. The components that are applicable to the system will then be visible. In all instances where a visible component is NOT part of the system being evaluated, its value must be defined as identical to that of the Reference value for a compliance calculation.
Cooling System Type | Choose the type of cooling equipment associated with this HVAC system as defined in Table 5.2.12.1 of the NECB.
Cooling Sub-System Type | Choose the precise category associated with the cooling equipment system type, as defined in Table 5.2.12.1 of the NECB.
Cooling capacity | This value only serves in defining the Reference value performance for certain type of cooling equipment, as defined in Table 5.2.12.1 of the NECB.
Heating System Type | Choose the type of heating equipment associated with this HVAC system as defined in Table 5.2.12.1 of the NECB. For all resistance electric heating cases, the user must select "Electric boilers". However, in this case, all of the components relating to the hot water distribution system must be defined using the Reference values.
Supply fan mechanical efficiency | Enter the supply fan design mechanical efficiency.
Supply motor efficiency | Enter the supply fan motor design efficiency.
Return fan mechanical efficiency | Enter the return fan design mechanical efficiency.
Return fan motor efficiency | Enter the return fan motor design efficiency.
Supply temperature control | Choose from the drop down list the type of supply temperature control applicable to this HVAC system.
Airflow control efficiency | Choose from the drop down list the type of supply airflow control applicable to this HVAC system.
Supply fan total static pressure | Enter the supply fan design total static pressure. It is important not to enter the external static pressure value, sometimes indicated on the equipment specifications.
Supply duct insulation | Enter the average insulation value for the supply ducts served by this HVAC system.
Return fan total static pressure | Enter the return fan design total static pressure. It is important not to enter the external static pressure value, sometimes indicated on the equipment specifications.
Heating coil design temperature drop | Enter the design temperature differential for the HVAC system heating coil. If multiple coils are present, use the capacity-weighted average value.
Baseboard heater design temperature drop | Enter the design temperature differential for the baseboard heaters.
Boiler/furnace/heat pump heating efficiency | Enter the heating equipment efficiency. For heat pumps, the COP must be expressed as fractions, such as 0.83 for 83% efficiency. For smaller equipment where only the AFUE is available, enter this value directly. If more than one piece of equipment is serving the system, enter the capacity-weighted average efficiency. If multiple energy sources are used, the fuel source of equipment providing the majority of the heating load must be selected.
Chillers/direct expansion system/heat pump cooling efficiency | Enter the cooling equipment efficiency. All efficiencies have to be entered in terms of COP. If more than one piece of equipment is serving the system, enter the capacity-weighted average efficiency.
Rejection fan input power ratio | Enter the heat rejection equipment unitary fan power. This value represents the ratio of the total installed fan power of the equipment divided by its heat rejection capacity, expressed in the same unit.
Cooling by direct use of outdoor air (air economizer) | Select the type of air-side economizer used in this HVAC system.
Outdoor airflow control | Select the type of outdoor air control used for this HVAC system (DCV = Demand control ventilation).
Exhaust air heat-recovery efficiency | Enter the design heat recovery effectiveness.
Cooling by indirect use of outdoor air (water economizer) | Enter the design water-side cooling coil heat exchange effectiveness.
Piping insulation - hot water | Enter the average piping insulation value.
Piping insulation - chilled water | Enter the average piping insulation value.
Piping pressure losses - hot water | Enter the total hydronic heating system pressure losses. In the case of multiple loops associated with a single HVAC system, enter the equivalent head calculated using the flow and head of each loop and expressed as an equivalent head for the loop having the largest flow rate.
Piping pressure losses - chilled water | Enter the total hydronic cooling system pressure losses. In the case of multiple loops associated with a single HVAC system, enter the equivalent head calculated using the flow and head of each loop and expressed as an equivalent head for the loop having the largest flow rate.
Pump mechanical efficiency - hot water | Enter the pump motor efficiency. When multiple pumps serve the system, use the power-weighted average pump efficiency.
Pump mechanical efficiency - chilled water | Enter the pump motor efficiency. When multiple pumps serve the system, use the power-weighted average pump efficiency.
Pump motor efficiency - hot water | Enter the design efficiency of the pump motor. When multiple pumps serve the system, use the power-weighted average motor efficiency.
Pump motor efficiency - chilled water | Enter the design efficiency of the pump motor. When multiple pumps serve the system, use the power-weighted average motor efficiency.
Hot water pump control | Select the hot water pump control logic applicable to this system.
Chilled water pump control | Select the chilled water pump control logic applicable to this system.
Hot water loop temperature control | Select the hot water temperature control logic applicable to this system.
Chilled water loop temperature control | Select the chilled water temperature control logic applicable to this system.
Hot water flow control | Select the hot water pump flow control applicable to this system. In the case where multiple pumps used different controls, select the type that controls the majority of the pump installed power.
Chilled water flow control | Select the chilled water pump flow control applicable to this system. In the case where multiple pumps used different controls, select the type that controls the majority of the pump installed power.
SWH Help Table
System Type | Select the system type that most closely matches the one being evaluated.
Equipment Type | Select the type of equipment used in producing the service hot water.
Tank Volume | Total volume of all storage tanks included in this system. Value must be equal or greater than 0.
Service water heating equipment efficiency | Enter the efficiency of the equipment used in producing the service hot water. For heat pumps, enter the COP in terms of %. For Efficiency Factors (EF), enter directly that value except for electric hot water tanks where an efficiency of 100% is to be used. If more than one equipment of the same type serves a system, enter the capacity-weighted average efficiency. Value must be greater than 0.
Tank insulation value | Define the tank's insulating value. For systems with multiple tanks, enter the surface-weighted average insulating value. Value must be between R 0.1 and 40 (RSI 0.5678-7.04).
Piping insulation value | Define the average piping insulation value for this service water heating system. Value must be between R 0.1 and 40 (RSI 0.5678-7.04).
Pump motor efficiency | Enter the efficiency of all pump motors used on this service water heating system. When multiple pumps are present, define the capacity-weighted average efficiency for all the pump motors. Value must be between 30% and 99%.
Pump efficiency | Enter the efficiency of all pumps ("pump efficiency" in this case refers to "pump mechanical efficiency") used on this service water heating system. When multiple pumps are present, define the capacity-weighted average efficiency for all the pumps. Value must be between 30% and 75%.
Heat recovery ratio | The installed recovery capacity divided by the total installed capacity of the SWH system, from the design specifications. If the heat recovery is limited to grey-water waste heat recovery then the installed recovery capacity is = Q * (Tin - Tout) * 4.182, where Q: flow rate (L/s), Tin: inlet temperature (warm) of the waste heat fluid (°C), Tout: outlet temperature (cold) of the waste heat fluid (°C). Value must be between 0 and 1. The conversion rate from litre per second to USGPM is 15.85
Average flow of all faucets | Enter the average flow rate of all faucets served by the service water heating system. Value must be greater than 0.1 and smaller than 4 gpm (0.006309 and 15.14 L/min).
Average flow of all showers | Enter the average flow rate of all shower heads served by the service water heating system. Value must be greater than 0.1 and smaller than 4 gpm (0.006309 and 15.14 L/min).
Faucet flow ratio | Define the typical weekly fraction of the hot water volume used by faucets through this service water heating system. Refer to standard calculation methods such as those presented in ASHRAE to evaluate this %. This value must be between 0% and 100%.
Shower flow ratio | Define the typical weekly fraction of the hot water volume used by showers through this service water heating system. Refer to standard calculation methods such as those presented in ASHRAE to evaluate this %. This value must be between 0% and 100%.
Average flow of other uses | Enter the average flow rates of all other appliances using hot water in this system. A default value of 7.6 L/min (2 gpm) can be used if other design data is unavailable. This value must be greater between 0 and 378.5 L/min and (100 gpm).

## Glossary-Glossaire
Glossary
OA | Outdoor Air
SPVAC | Single Package Vertical Air Conditioner
SPVHP | Single Package Vertical Heat Pump
PTHP | Packaged Terminal Heat Pump
PTAC | Packaged Terminal Air Conditioner
VSD | Variable Speed Drive
DCV | Demand Control Ventilation
DBT | Dry Bulb Temperature
VAV | Variable Air Volume